## Cover
| TesysTera_Modbus_IFD |  | 2025-04-17
Modbus Map
2.6
DOCUMENT HISTORY
Ver./Rel. No | Release Date | Mod.By Mod. Dt | Remarks/Revision Details
2 | 2022-01-22 | NH | Initial draft for review
2022-01-22
2.01 | 2022-04-12 | SV | 1. Changed address of motor start - reference log 2. Starting address changed for product info 3. Address changed of read write data for internal data 4. Function code corrected for TesysT parameters.
2022-04-12
2.02 | 2022-04-26 | AL | 1.Monitoring Data: Motor Data--> "Mode Transfer" motor stop cause added. Range 0-13 changed. 2.Protection sheet-Alarm level changed in terms of %IFLC
2.03 | 2022-05-19 | NH | General Settings: 1.Device configuration updated for commercial references 2.Modbus settings updated 3. Ethernet settings added 4. System settings updated Protection settings: 1. Address corrected for control functions Product Info: 1. Detected modules updated
2.04 | 2022-05-23 | SV/NH | TeSys T Parameters: 1. Command register details updated 2. Address and size updated for global statistic parameters
2.05 | 2022-07-12 | NH | General Settings: 1.Device configuration updated for US commercial references 2.Ethernet settings updated as per DTM team comments 3. Ethernet settings added 4. System settings - 'secondary passes' parameter added Product Info: 1. Detected modules updated for US commercial references Internal Data: Manufacturing test settings added Protection settings: 1. voltage dip functions parameters updated Status: 1. Protection names updated as per TeSys Tera dictonary Added Settings-interlocks sheet
2.06 | 2022-09-05 | AL | General Settings: 1. DO Settings: DO Input source Max range is updated to 65535 2. Disaplay settings name changed to HMI settings TeSys T Parameters: 1. TesysTera CL DO Input Information parameter added. 2. Mode selection 1&2 parameters added in Command register 1. 3. General configuration register 1parameter added for system configuration mode. 601 4. Trip enable register 2 , Alarm enable register 2, Permissive Commands parameters added Monitoring Data: 1. Custom Logic DI Status parameter added for starter logic. Interlock settings sheet: 1. Interlock formulas updated DO_CompLogic_List Added - Refer for DO input source and Comp logic settings input, Updated for Custom logic.
2.07 | 2022-10-02 | AL,NH | Internal Data: 1. Firmware Update Status and Commands added for firmware update TeSys T Parameters: User defined map settings max limit updated Protection settings: 1. Measured earth current protection pickup and alarm range updated
2.08 | 2022-11-07 | AL,NH | Internal Data: 1. Firmware Update Status , firmware Update error and Commands added for firmware update 2. RTC calibration registers updated Monitoring Data: 1. PTC register renamed and unit is updated 2. Parameter name updated as per Safety norms General Settings: 1. Device Configuration: Sensor module commercial reference is updated as per Offer Marketing rev V5 2. Parameter name updated as per Safety norms Product Info: 1. Detected Modules: Sensor module commercial reference is updated as per Offer Marketing rev V5 Protection Settings: 1. Parameter name updated as per Safety norms DO_CompLogic_list: 1. Parameter name updated as per safery norms 2. Do list highlighted with Green for Qatar gas All sheets: Updated data type
2.09 | 2022-11-15 | AL,NH | Protection Settings: 1. Excessive start time: Multiplier updated for RUN threshold Internal Data: 2. Firmware Update Status , firmware Update error and Commands added for firmware update
2.1 | 2022-11-21 | SS | Monitoring Data: - Added parameters for Extended Monitoring Data General Settings: - Added Configuration parameter for Product Profile Selection in Profibus Settings. User defined Map: - Added User Define Mapping for Status Word Parameters
2.11 | 2022-12-07 | NH | General Settings: - Device configuration: commercial reference list and max index updated Product Info: - Detected Expansion: commercial reference list and max index updated Interlock sheet: - Commercial reference list updated
2.12 | 2022-12-08 | NH,AL | Internal Data: 1. Firmware Update Success Status added.
2.13 | 2023-01-31 | NH,AL | Status: 1. Firmware Update Inhibit added.
2.14 | 2023-02-18 | NH,AL | 1. CompLogic Settings: Timer Settings address starts from 5375. 2. TeSys T Parameters: 1301-1399 address enabled for write operation. 3. Protection Settings: - Thermal overload default settings updated - Normal inverse Time delay settings label updated - AI protection min settings updated 4. General Settings: - Device Configuration expansion settings updated - System settings updated 5. Monitoring Data: - Motor stop cause list updated 6. Status - Custom logic DI status added 7. Product info sheet - Strings updated firmware, boot version
2.15 | 2023-02-22 | NH | 1. General Settings: - Device Configuration sensor module default settings updated 2. Monitoring Data: - Permissive commands status added in boolean data
2.16 | 2023-03-08 | NH.AL | Status: Communication Status-Modbus RTU Port and HMI port no communication bits added Monitoring Data: Boolean Data- Communication Status register added
2.17 | 2023-04-05 | NH.AL | General Settings: AO settings reserved added to resolve padding issue
2.18 | 2023-05-05 | NH,AL | TeSys T Parameters: - Communication Motor Stop command bit added. - General configuration register 2 added Protection Settings: - Trip word renamed as fault. - Hysteresis Settings updated - Temperature Protections Pickup and Alarm range modified - Diagnostic bytes added in Analog and Temperature protection - HMI communication loss settings added General Settings: - Profibus, Modbus and HMI communication settings updated - Communication Start Input parameter added. - Number of Phases parameter added. - AO settings and table 5 updated. - Motor Name Plate Details added - VT Primary & Secondary Removed. Voltage Nominal added. - Default settings changed - System settings -> CTP, CTS, IFLC, Monitoring Data: - Motor Stop Cause updated
2.19 | 2023-05-10 | NH,AL | Product Info: - Standard Package Version details added Monitoring Data: - Motor Stop Cause updated Protection Settings: - Excessive Start Time, Time delay parameter default value updated
2.2 | 2023-05-18 | NH,AL | Status: - Comp Logic - Motor Indicators modified
2.21 | 2023-06-29 | NH,AL | Monitoring Data: - Extended Monitoring Data: Multipliers upadted. User defined Map: -Minimum and default value updated
2.22 | 2023-07-21 | NH,AL | Protection Settings: - ICM Detection protection updated CompLogic Settings: - Calculator settings added Monitoring Data- - Calculator Output added Status: - Internal Relay Fault Pickup & Trip bits added
2.23 | 2023-08-30 | NH,AL | Status: - Comp Logic - Motor Indicators modified Starter settings: -Load type setting removed
2.24 | 2023-09-11 | NH,AL | Status: - 5Input2Output TT 2 bits updated DO_CompLogic_List: - 5Input2Output TT 2 bits updated
2.25 | 2023-09-15 | NH,AL | Product Serial Number : - New sheet added for Serial numbers of sensor and expansion modules CompLogic Settings: - Analog comparator Settings added Monitoring Data: -Boolean Data-Analog comparator Output Status added Status: - Analog comparator bits updated DO_CompLogic_List: - Analog comparator bits updated
2.26 | 2023-10-11 | NH | TeSys T Parameters: - HMI registers updated General Settings: - HMI control keys setting added in HMI settings Internal Data: - Bit Added for HMI programmable key Configuration
2.27 | 2024-01-02 | NH | Protection settings: - Alarm level added for current and voltage Imbalance protection General settings: - Load type setting restored in Starter settings - Minimum value updated for Nominal power in Motor name plate DO_CompLogic_List: - Updated for ICM and HMI communication loss protection - Updated for truth table outputs Status: - Updated for ICM and HMI communication loss protection - Updated for truth table outputs
2.28 | 2024-01-11 | NH | Product Info: - Hardware version format changed to ASCII
2.29 | 2024-04-13 | NH | Product Info: - Monitoring Data: Locked rotor and stalled rotor trip counter sequence corrected in statistic data General Settings: - System settings updated for CT and IFLC settings - Device configuration is updated for sensor module commercial referene
2.3 | 2024-04-16 | NH | Settings Interlock: - Updated for 3A sensor module User defined map: - Configuration range updated
2.31 | 2024-04-23 | NH | General Settings: - Session management settings added DO_CompLogic_List: - ICM Inhibit bit removed Status: - ICM Inhibit bit removed in Inhibit status
2.32 | 2024-05-28 | NH | General Settings: - DI settings validation time step size updated - DO settings pulse time step size updated Protection Settings: - Thermal overload disable option added
2.33 | 2024-06-06 | NH | General Settings: - Range and default value updated for session timeout
2.34 | 2024-06-12 | NH | Protection Settings: - Fallback setting added (Inactive) DO_CompLogic_List - Alarm, pickup and trip staus is updated for ICM and HMI communication loss protection
2.35 | 2024-07-09 | NH,AL | Status: - TTE-665, TTE-655 - Internal temperature major error detected added - Internal temperature minor error detected added DO_CompLogic_List: - TTE-665, TTE-664, TTE-655 Protection Settings: - TTE-527 - ICM Detection- Internal Temperature Warning Enable setting added TeSys T Parameters: - TTE-589 - Monitoring Variables: Controller internal temperature (°C) added - Global Statistics: Controller internal temperature max (°C) added General Settings: -Function code updated for AO settings Monitoring Data: - TTE-613
2.36 | 2024-07-12 | NH | sheet name renamed: Product serial number -> Product Info - Extended Protection settings: - Updated for temperature unit - TTE-548: ICM renamed as Device Internal Monitoring Data: - Updated for temperature unit - TTE-548: ICM renamed as Device Internal DO_CompLogic List: - TTE-548: ICM renamed as Device Internal Status: - TTE-548: ICM renamed as Device Internal General setting: - DO Tag list updated for TTE-548 Product Info - Extended: - Updated for TTE-660 module tag
2.37 | 2024-07-30 | NH | Monitoring Data: - TTE-541: L1-L2 voltage updated for single phase as well (L1-N) General setting: - AO input source list updated for TTE-541
2.38 | 2024-08-02 | VR | 1) Sheet Modified: TeSys T Parameters Mirroring Variables added 2) sheet added Ethernet settings, EIP DETAILS, EIP Cyclic Parameter,EIP Object Overview 3) Shee Modified: Internal Data MAC address for Write,PDD test byte 4) Sheet Modified: Product Info EIP Product Details 5) Sheet Modify: Status: Communication Status - NTP Not working, DHCP IP assignment Fail, Port 1 Link Fail, Port 2 Link Fail 6) Sheet Modified: Ethernet Settings: Daylight saving settings added
2.39 | 2024-08-01 | NH | Monitoring Data: - TTE-575: Active trip and alarm counter added
2.4 | 2024-08-16 | NH | Monitoring Data: - TTE-759: Three trip counters added in statistic data
2.41 | 2024-08-17 | NH | General settings: - TTE-768: default setting of direction change is updated in starter settings
2.42 | 2024-09-09 | VR | Ethernet Settings: 1) Name of EDS profile changed from T6T to Tera 2) Syslog filter category and syslog_export_filter_severity replaced by Modbus HMI and TCP Selection added 3) Minimum value of gateway byte 3 changed to 0 4) Minimum value fo IP byte 3changed to 0 5) Default value of gateway byte 3 made 0 6) Minimum value of ntp server byte 3 is changed to 0 7) Default value of ntp server byte 3 is made to 0 8) Default Subnet mask changed to 255.255.255.0 to 255.2555.0.0. 9) Maximum value of Day in daylight saving is changed from 4 to 5 for both start day and end day 10) Default & Max value of Modbus Unit TCP is changed to 255 from 1 11) Modbus TCP port is configurable variable added
2.43 | 2024-09-09 | VR | 1) TeSys T Monitoring Control Object 0xC6 ---Default instance attribute value is 455,456,457,458 --- Primaray and secondary server for NTP/stnp is added in ethernet settings --- Secondary NTP//SNTP server added in ethernet setting sheet --- Default value of gate way changes to keep in synch with valid ip logic --- Minimum value of default gateway byte 0 is changed to 0 --- FDR back up period minimum settings is changed from 0 to 30. --- Change in direction in General Setting : default value made it to 0 --- Change in the string name of Motor Tag to User Application in general setting sheet General Settings: - Device configuration Exp settings updated for PTC configuration - System settings: voltage input default value updated to 1 (Enable) TTE-863 Protection settings: - Thermal overload Reset Mode max value updated TTE-795 General Settings: - Unused DI source default change to NONE(38) TTE-828 - RTC : default Year value changed to 2024
2.44 | 2024-12-23 | VR | 1) Diagnostic Addressing changed
2.45 | 2025-01-04 | VR | 1) Diagnostic heaading changed to Data address
2.46 | 2025-01-24 | VR | Internal Data sheet 1) HMI FDR bit added 2) Device Internal min value chaged to 1
2.47 | 2025-03-03 | VR | Internal Data sheet 1) Modbus TCP Reset register Ethernet Setting 1) DPWS Default value changed to enable Monitoring 1) PTC fahrenheit range added as note Protection 1) Temperature (Main Unit) fahrenheit range added as note
2.48 | 2025-03-17 | VR | EIP DETAILS 1) TCP/IP objects instance attributes list updated
2.49 | 2025-03-21 | VR | TeSys T Parameters: - Min, max, step size and multiplier updated Protection settings: - NI over current protection - Time delay replaced with Time Multiplier. Unit 'Seconds' removed. General Settings: - Table 5 updated max value for frequency is updated. EIP Detail - TCP Class attribute values infor added EIP Cyclic - Instance 51 Trip Reset Typo updated Ethernet Setting - Default Setting of DNS changed to 1 Protection Setting - Comm Loss Protection function Default changed to alarm+Trip
2.5 | 2025-05-14 | VR | Monitoring - Motor stop cause strings updated EIP Object Overview - Motor Tag name changed to User Application Name
2.51 | 2025-05-21 | VR | Ethernet Settings: 1) Slave id min is changed to 1 Tesyst Parameters -- Trip registers updated as per Tera Serial release 2.0.8 -- Alarm Registers are updated as per Tera Serial Release 2.0.8
2.52 | 2025-07-08 | VR | Protection -- AI protection diganostic bit changed to reserved
2.53 | 2025-08-05 | VR | General Settings : Custom Logic starter added in Table 2
2.54 | 2025-08-26 | VR | General Setting: Table 6: Overload: Do3 Active Type Value changed to 0 to 1
2.55 | 2025-10-06 | VR | Protection Setting: Device Internal: Reserved default value change to 0 : Internal Temperature
2.56 | 2025-10-31 | VR | Ethernet Settings: IP allow list data not needed to update over modbus register : it is kept of development future refernce (TTET-1013)
2.57 | 2025-11-13 | VR | Product Info: Product Code: Word size increase to 2 from 1
2.58 | 2025-11-19 | VR | Status-> Internal controller malfunction detection - Main Controller-> HMI Comm Error Detected changed to Reserved(TTET-264)
2.59 | 2025-11-26 | VR | Status-> Protection Pickup Status -> Excessive Start Time Pickup changed to Reserved,
Status-> Protection Trip Status -> Excessive Start Time Trip changed to Reserved,
Protection Settings-> Excessive Start Function -> Min Max updated
DO_CompLogic_List -> Excessive Start Time Pickup changed to Reserved,
DO_CompLogic_List -> Excessive Start Time Trip changed to Reserved(TTET-1103).
DO_CompLogic_List -> HMI communication error detected changed to Reserved(TTET-264)
2.6 | 2026-04-17 | VR | 1) EIP Cyclic Parameter : Comment Added for RUN1 and RUN2 bits 2) EIP Cyclic Parameter : Register 704 , bit 1 changed to Reserved 3) Product Info: Version information added for Internal Purpose only

## EIP Object Overview
Tesys T |  |  | Tesys Tera
Variable Groups | Modbus/TCP (Register addresses) | EtherNet/IP (Object addresses) | Group name | EtherNet/IP (Object addresses) | Group | Service Type
Identification variables | 00 to 99 | 64 : 01 : 32 to 64 : 01 : 61 | Tera Product Info
Statistics variables | 100 to 449 | 65 : 01 : 01 to 67 : 01 : 83 | TeSys T Parameters->global stats+ LTM Monitor stats+Trip stats+Trip Ext. | 65 : 01 : 01 to 67 : 01 : 9A | Global+Monitor+trip+trip ext stats | Get Single, Get All
Monitoring variables | 450 to 539 | 68 : 01 : 01 to 68 : 01 : 4A | TeSys T Parameters->Monitoring variable | 68 : 01 : 01 to 68 : 01 : 5B | Monitoring variable | Get Single, Get All
Configuration variables | 540 to 699 | 69 : 01 : 01 to 6B : 01 : 32 | TeSys T Parameters-> Configuration variable + Settings | 69 : 01 : 01 to 6B : 01 : 33 | Configuration variable: 0x69 not needed | Get Single, Get All, Set single
Command variables | 700 to 713 | 6C : 01 : 01 to 6C : 01 : 0A | TeSys T Parameters-> Commands | 6C : 01 : 01 to 6C : 01 : 07 | Commands | Get Single, Get All, Set Single, Set all
User map variables | 800 to 999 | 6D : 01 : 01 to 6E : 01 : 64 | TeSys T Parameters->User map address + User map Values | 6D : 01 : 01 to 6E : 01 : 64 | User map address, User map values | Get Single, Get All, Set Single, Set all
Custom logic variables | 1250 to 1399 | 71 : 01 : 33 to 71 : 01 : C8 | TeSys T Parameters->Custom Logic Variables | 71 : 01 : 33 to 71 : 01 : C8 | Custom logic | Get Single, Get All, Set single
Extended monitoring variables for communication | 2000 to 2099 | 82 : 01 : 01 to 82 : 01 : 27 | Not needed: Tera internal data
Mirroring variables | 2500 to 2599 | 8C : 01 : 01 to 8C : 01 : 15 | TeSys T Parameters->Mirroring Variable | 8C : 01 : 01 to 8C : 01 : 09 | Mirroring | Get Single, Get All, Set single
Extended configuration variables for communication | 3000 to 3120 | 96 : 01 : 01 to 96 : 01 : 77 | Tera Eth Config
Service Name | Service Code(Hex) |  | TeSys Tera Parameter |  | Serivce Type
Get All | 0x01 |  | Monitoring Data | 72 : 01 : 01 to 72 : 09 : 30
Set All | 0x02 | Group 1 | Metering Data | 72 : 01 : 01 to 72 : 01 : 21 | Get Single, Get All
Get Single | 0x0E |  | Motor Data | 72 : 02 : 01 to 72 : 02 : 0E | Get Single, Get All
Set Single | 0x10 |  | Last Motor Time stamp | 72 : 03 : 01 to 72 : 03 : 07 | Get Single, Get All
|  |  | Analog Module data | 72 : 04 : 01 to 72 : 04 : 0C | Get Single, Get All
|  |  | Temperature Module Data | 72 : 05 : 01 to 72 : 05 : 0F | Get Single, Get All
|  |  | Boolean Data | 72 : 06 : 01 to 72 : 06 : 1D | Get Single, Get All
Class Name | Class Code |  | Statistic Data | 72 : 07 : 01 to 72 : 07 : 4E | Get Single, Get All
|  |  | Extended Monitoring Data | 72 : 08 : 01 to 72 : 08 : 17 | Get Single, Get All
Identity Object | 0x01 | Group 2 | Product Info+Extended Product Info | 73 : 01 : 01 to 73 : 01 : 41 | Get Single, Get All
Message Router Object | 0x02 |  | Status: not needed taken care in Boolean Data | 80 : 01 : 01 to 80 : 01 : 20
Assembly Object | 0x04
Connection Manager Object | 0x06 |  | User Define Map: not needed as taken care in Extended Monitoring Data | 80 : 01 : 01 to 80 : 01 : 02
QoS Object | 0x48
TCP/IP Object | 0xF5 |  | Data record | 82 : 01 : 01 to 82 : 41 : 01
Ethernet Link Object | 0xF6 | Group 3 | Fault Record: 20 | 82 : 01 : 01 to 82 : 14 : 01 | Get All
Control Supervisor Object | 0x29 |  | Event Record: 100 | 82 : 15 : 01 to 82 : 78 : 01 | Get All
Overload Object | 0x2C |  | Internal Fault: 20 | 82 : 79 : 01 to 82 : 8C : 01 | Get All
Periodically Kept Acyclic Words (PKW) Objects | 0xC5 |  | Motor Start-Latest Log | Not needed for EIP since it was used to plot the curve
TeSys T Monitoring Control Object | 0xC6 |  | Motor Start-Reference Log | Not needed for EIP since it was used to plot the curve
Stack Diagnostic Object | 0x300
Adapter Diagnostic Object | 0x302 |  | Protection Settings | 83 : 01 : 01 to 84 : 04 : 06
Explicit Messages Diagnostic Object | 0x0303 | Group 4 | Current | 83 : 01 : 01 to 83 : 01 : 5B | Get Single, Get All, Set Single, Set all
Explicit Message Diagnostic List Object | 0x0304 |  | Voltage | 83 : 02 : 01 to 83 : 02 : 43 | Get Single, Get All, Set Single, Set all
LLDP Management Object | 0x109 |  | Control | 83 : 03 : 01 to 83 : 03 : 3D | Get Single, Get All, Set Single, Set all
LLDP Data Table Object | 0x10A | Group 5 | Interlock DI | 84 : 01 : 01 to 84 : 01 : 3C | Get Single, Get All, Set Single, Set all
Identification variables | 0x64 |  | AI | 84 : 02 : 01 to 84 : 02 : 20 | Get Single, Get All, Set Single, Set all
Statistics variables | 0x65-0x67 |  | Temp | 84 : 03 : 01 to 84 : 03 : 78 | Get Single, Get All, Set Single, Set all
Monitoring variables | 0x68 |  | Hysteresis | 84 : 04 : 01 to 84 : 04 : 06 | Get Single, Get All, Set Single, Set all
Configuration variables | 0x69-0x6b |  | General Settings | 85 : 01 : 01 to 86 : 03 : 16
Command variables | 0x6C | Group 6 | Device | 85 : 01 : 01 to 85 : 01 : 12 | Get Single, Get All, Set Single, Set all
User map variables | 0x6D-0x6E |  | HMI | 85 : 02 : 01 to 85 : 02 : 06 | Get Single, Get All, Set Single, Set all
Custom logic variables | 0x71 |  | RTC | 85 : 03 : 01 to 85 : 03 : 09 | Get Single, Get All, Set Single, Set all
Extended monitoring variables for communication | 0x82 |  | Starter | 85 : 04 : 01 to 85 : 04 : 20 | Get Single, Get All, Set Single, Set all
Mirroring variables | 0x8C |  | System | 85 : 05 : 01 to 85 : 05 : 17 | Get Single, Get All, Set Single, Set all
Extended configuration variables for communication | 0x96 |  | User Application | 85 : 06 : 01 to 85 : 06 : 0B | Get Single, Get All, Set Single, Set all
|  |  | Password Management | 85 : 07 : 01 to 85 : 05 : 01 | Get Single, Get All, Set Single, Set all
|  | Group 7 | DI | 86 : 01 : 01 to 86 : 01 : 60 | Get Single, Get All, Set Single, Set all
|  |  | DO | 86 : 02 : 01 to 86 : 02 : 46 | Get Single, Get All, Set Single, Set all
|  |  | AO | 86 : 03 : 01 to 86 : 03 : 16 | Get Single, Get All, Set Single, Set all
|  |  | Complogic | 87 : 01 : 01 to 87 : 0A : 05
|  | Group 8 | 2IP1OP TT | 87 : 01 : 01 to 87 : 01 : 06 | Get Single, Get All, Set Single, Set all
|  |  | 3IP1OP TT | 87 : 02 : 01 to 87 : 02 : 20 | Get Single, Get All, Set Single, Set all
|  |  | 5IP2OP TT | 87 : 03 : 01 to 87 : 03 : 12 | Get Single, Get All, Set Single, Set all
|  |  | 4IP1OP TT | 87 : 04 : 01 to 87 : 04 : 45 | Get Single, Get All, Set Single, Set all
|  |  | Timer | 87 : 05 : 01 to 87 : 05 : 10 | Get Single, Get All, Set Single, Set all
|  |  | Signal Conditioner | 87 : 06 : 01 to 87 : 06 : 0C | Get Single, Get All, Set Single, Set all
|  |  | Non volatile | 87 : 07 : 01 to 87 : 07 : 0C | Get Single, Get All, Set Single, Set all
|  |  | Counter | 87 : 08 : 01 to 87 : 08 : 10 | Get Single, Get All, Set Single, Set all
|  |  | LED: Not Required | 87 : 09 : 01 to 87 : 09 : 03
|  |  | Custom Starter | 87 : 09 : 01 to 87 : 09 : 05 | Get Single, Get All, Set Single, Set all
|  |  | Calculator | 87 : 0A : 01 to 87 : 0A : 0E | Get Single, Get All, Set Single, Set all
|  |  | Analogue Comparator | 87 : 0B : 01 to 87 : 0B : 1C | Get Single, Get All, Set Single, Set all
|  |  | User Defined Status Words | 87 : 0A : 01 to 87 : 0A : 20 | Get Single, Get All, Set Single, Set all
|  | Group 9 | General Settings | 88 : 0A : 01 to 87 : 0A : CF
|  |  | Ethernet settings | 88 : 01 : 01 to 88 : 01 : CF | Get Single, Get All,(Timezone, NTPSelection and dst are RW with Set Single and Set All)

## TeSys T Parameters
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Global Statistics
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 101 | 100 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 102 | 101 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 103 | 102 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 104 | 103 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 105 | 104 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 106 | 105 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 107 | 106 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 108 | 107 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 109 | 108 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 110 | 109 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 111 | 110 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 112 | 111 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 113 | 112 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 114 | 113 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 115 | 114 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 116 | 115 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 117 | 116 | 0x03 | N
Motor starts count | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 118 | 117 | 0x03 | Y | 0
Motor Operating time | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 120 | 119 | 0x03 | Y | 0 | Seconds
Controller internal temperature max (°C) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 122 | 121 | 0x03 | N | 0 | Deg. Celcius
LTM monitoring Statistics
Trip Count | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 123 | 122 | 0x03 | Y | 0
Alarm Count | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 124 | 123 | 0x03 | Y | 0
Motor LO1 Closing count | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 125 | 124 | 0x03 | Y | 0
Motor LO2 Closing count | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 127 | 126 | 0x03 | Y | 0
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 129 | 128 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 130 | 129 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 131 | 130 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 132 | 131 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 133 | 132 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 134 | 133 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 135 | 134 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 136 | 135 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 137 | 136 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 138 | 137 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 139 | 138 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 140 | 139 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 141 | 140 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 142 | 141 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 143 | 142 | 0x03 | N
Active Power Consumption | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 144 | 143 | 0x03 | Y | 0 | kWh
Reactive Power Consumption | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 146 | 145 | 0x03 | Y | 0 | kVARh
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 148 | 147 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 149 | 148 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 150 | 149 | 0x03 | N
Trip statistics
Last trip statistics | UINT16 | 60 | 30 |  |  |  |  | R | 151 | 150 | 0x03 | N |  |  | Refer Table 1
Trip n-1 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 181 | 180 | 0x03 | N |  |  | Refer Table 1
Trip n-2 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 211 | 210 | 0x03 | N |  |  | Refer Table 1
Trip n-3 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 241 | 240 | 0x03 | N |  |  | Refer Table 1
Trip n-4 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 271 | 270 | 0x03 | N |  |  | Refer Table 1
trip statistics - Extention
Last trip extention | UINT16 | 60 | 30 |  |  |  |  | R | 301 | 300 | 0x03 | N |  |  | Refer Table 2
Trip n-1 extention | UINT16 | 60 | 30 |  |  |  |  | R | 331 | 330 | 0x03 | N |  |  | Refer Table 2
Trip n-2 extention | UINT16 | 60 | 30 |  |  |  |  | R | 361 | 360 | 0x03 | N |  |  | Refer Table 2
Trip n-3 extention | UINT16 | 60 | 30 |  |  |  |  | R | 391 | 390 | 0x03 | N |  |  | Refer Table 2
Trip n-4 extention | UINT16 | 60 | 30 |  |  |  |  | R | 421 | 420 | 0x03 | N |  |  | Refer Table 2
Monitoring Variables
Minimum wait time | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 451 | 450 | 0x03 | N | 0 | Seconds
Trip code | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 452 | 451 | 0x03 | N | 0
Trip register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 453 | 452 | 0x03 | N |  |  | bits 0-1 (Reserved) bit 2 Ground current fault bit 3 Thermal overload fault bit 4 Long start fault bit 5 Jam fault bit 6 Current phase imbalance fault bit 7 Undercurrent fault bit 8 (Reserved) bit 9 Test fault bit 10 HMI port fault bit 11 Controller internal fault bit 12 Internal port fault bit 13 (Not significant) bit 14 Network port config fault bit 15 Network port fault
Trip register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 454 | 453 | 0x03 | N |  |  | bit 0 External system fault bit 1 Diagnostic fault bit 2 Wiring fault bit 3 Overcurrent fault bit 4 Current phase loss fault bit 5 Current phase reversal fault bit 6 Motor temperature sensor fault bit 7 Voltage phase imbalance fault bit 8 Voltage phase loss fault bit 9 Voltage phase reversal fault bit 10 Undervoltage fault bit 11 Overvoltage fault bit 12 Underpower fault bit 13 Overpower fault bit 14 Under power factor fault bit 15 Over power factor fault
Trip register 3 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 455 | 454 | 0x03 | N
System Status register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 456 | 455 | 0x03 | N |  |  | bit 1 System on bit 2 System fault bit 3 System warning bit 4 System tripped bit 5 Fault reset authorized bit 6 Controller power bit 7 Motor running (with detection of a current, if greater than 10% FLC) bits 8-13 Motor average current ratio 32 = 100% FLC - 63 = 200% FLC bit 14 In remote bit 15 Motor starting (start in progress) 0 = descending current is less than 150% FLC 1 = ascending current is greater than 10% FLC
System Status register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 457 | 456 | 0x03 | N |  |  | bit 0 Auto-reset active bit 1 (Not significant) bit 2 Fault power cycle requested bit 3 Motor restart time undefined bit 4 Rapid cycle lockout bit 5 Load shedding bit 6 Motor speed 0 = FLC1 setting is used 1 = FLC2 setting is used bit 7 HMI port comm loss bit 8 Network port comm loss bit 9 Motor transition lockout bits 10-15 (Not significant)
Logic Input status register | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 458 | 457 | 0x03 | N
Logic Output status register | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 459 | 458 | 0x03 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | R | 460 | 459 | 0x03 | N
Alarm Code | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 461 | 460 | 0x03 | N
Alarm Register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 462 | 461 | 0x03 | N |  |  | bits 0-1 Reserved bit 2 Ground current warning bit 3 Thermal overload warning bit 4 Reserved bit 5 Jam warning bit 6 Current phase imbalance warning bit 7 Undercurrent warning bits 8-9 Reserved bit 10 HMI port warning bit 11 Controller internal temperature warning bits 12-14 (Not significant) bit 15 Network port warning
Alarm Register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 463 | 462 | 0x03 | N |  |  | bit 0 (Not significant) bit 1 Diagnostic warning bit 2 (Reserved) bit 3 Overcurrent warning bit 4 Current phase loss warning bit 5 Current phase reversal warning bit 6 Motor temperature sensor warning bit 7 Voltage phase imbalance warning bit 8 Voltage phase loss warning bit 9 Reserved bit 10 Undervoltage warning bit 11 Overvoltage warning bit 12 Underpower warning bit 13 Overpower warning bit 14 Under power factor warning bit 15 Over power factor warning
Alarm Register 3 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 464 | 463 | 0x03 | N
Motor Temperature sensor degree | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 465 | 464 | 0x03 | N |  | deg. C
Thermal capacity level | UINT16 | 2 | 1 | 0 | 1000 | 1 | 1 | R | 466 | 465 | 0x03 | N |  | %TM
Average current ratio | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 467 | 466 | 0x03 | N |  | %IFLC
L1 Current ratio | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 468 | 467 | 0x03 | N |  | %IFLC
L2 Current ratio | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 469 | 468 | 0x03 | N |  | %IFLC
L3 Current ratio | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 470 | 469 | 0x03 | N |  | %IFLC
Ground Current Ratio | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 471 | 470 | 0x03 | N |  | %FLC
Current Phase Imbalance | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 472 | 471 | 0x03 | N |  | %
Controller internal temperature (°C) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 473 | 472 | 0x03 | N |  | °C
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | R | 474 | 473 | 0x03 | N
Frequency | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 475 | 474 | 0x03 | N |  | Hz
Motor Temperature Sensor Ohm | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 476 | 475 | 0x03 | N |  | Ohm
Average Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 477 | 476 | 0x03 | N |  | V
L3-L1 Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 478 | 477 | 0x03 | N |  | V
L1-L2 Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 479 | 478 | 0x03 | N |  | V
L2-L3 Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 480 | 479 | 0x03 | N |  | V
Voltage Phase Imbalance | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 481 | 480 | 0x03 | N |  | %
Power Factor | UINT16 | 2 | 1 | 0 | 100 | 1 | 1/100 | R | 482 | 481 | 0x03 | N
Active Power | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 483 | 482 | 0x03 | N |  | kW
Reactive Power | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 484 | 483 | 0x03 | N |  | kVAR
Auto Restart Status Register | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 485 | 484 | 0x03 | N
Controller Last PowerOff Duration | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 486 | 485 | 0x03 | N |  | s
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 487 | 486 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 488 | 487 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 489 | 488 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 490 | 489 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 491 | 490 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 492 | 491 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 493 | 492 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 494 | 493 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 495 | 494 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 496 | 495 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 497 | 496 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 498 | 497 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 499 | 498 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 500 | 499 | 0x03 | N
Average Current | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/100 | R | 501 | 500 | 0x03 | N | A
L1 Current | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/100 | R | 503 | 502 | 0x03 | N | A
L2 Current | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/100 | R | 505 | 504 | 0x03 | N | A
L3 Current | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/100 | R | 507 | 506 | 0x03 | N | A
Ground Current | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/1000 | R | 509 | 508 | 0x03 | N | A
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 511 | 510 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 512 | 511 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 513 | 512 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 514 | 513 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 515 | 514 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 516 | 515 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 517 | 516 | 0x03 | N
Reserved | UINT16 | 46 | 23 |  |  |  |  | R | 518 | 517 | 0x03 | N
Configuration variables
Reserved | UINT16 | 122 | 61 | 0 | 0 | 0 | 0 | RW | 541 | 540 | 0x03,0x06,0x10 | N
General configuration register 1 | BITMAP | 2 | 1 | 0 | 1 | 1 | 1 | RW | 602 | 601 | 0x03,0x06,0x10 | Y | 0 |  | bit 0 Controller system config required 0 = exit the configuration menu 1 = go to the configuration menu
General configuration register 2 | BITMAP | 2 | 1 | 0 | 2048 | 2048 | 1 | RW | 603 | 602 | 0x03,0x06,0x10 | Y | 0 |  | bits 0-10(Reserved) bit 11: HMI motor status LED color 0: Red 1:Green bits 12-15 (Reserved)
Reserved | UINT16 | 56 | 28 | 0 | 0 | 0 | 0 | RW | 604 | 603 | 0x03,0x06,0x10
Trip enable register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 632 | 631 | 0x03,0x06,0x10 | Y |  |  | bits 0-1 (Reserved) bit 2 Calculated ground trip fault enable bit 3 Thermal overload fault enable bit 4 Long start fault enable bit 5 Stalled Rotor fault enable bit 6 Current phase imbalance fault enable bit 7 Undercurrent fault enable bit 8 (Reserved) bit 9 Self test enable 0 = disable 1 = enable (factory setting) bit 10 HMI port fault enable bits 11-14 (Reserved) bit 15 Network port fault enable
Alarm enable register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 633 | 632 | 0x03,0x06,0x10 | Y |  |  | bit 0 (Not significant) bit 1 (Reserved) bit 2 Calculated ground trip warning enable bit 3 Thermal overload warning enable bit 4 (Reserved) bit 5 Stalled Rotor warning enable bit 6 Current phase imbalance warning enable bit 7 Undercurrent warning enable bits 8- 9 (Reserved) bit 10 HMI port warning enable bit 11 Controller internal temperature warning enable bits 12-14 (Reserved) bit 15 Network port warning enable
Trip enable register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 634 | 633 | 0x03,0x06,0x10 | Y |  |  | bit 0 (Reserved) bit 1 Diagnostic fault enable bit 2 Wiring fault enable bit 3 Overcurrent fault enable bit 4 Current Phase loss fault enable bit 5 Current Phase reversal fault enable bit 6 Temperature (Main Unit) fault enable bit 7 Voltage imbalance fault enable bit 8 Voltage+Q130 phase loss fault enable bit 9 Voltage phase reversal fault enable bit 10 Undervoltage fault enable bit 11 Overvoltage fault enable bit 12 Underpower fault enable bit 13 Overpower fault enable bit 14 Under power factor fault enable bit 15 Over power factor fault enable
Alarm enable register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 635 | 634 | 0x03,0x06,0x10 | Y |  |  | bit 0 (Reserved) bit 1 Diagnostic warning enable bit 2 (Reserved) bit 3 Overcurrent warning enable bit 4 Current Phase loss warning enable bit 5 (Reserved) bit 6 Temperature (Main Unit) warning enable bit 7 Voltage imbalance warning enable bit 8 Voltage phase loss warning enable bit 9 (Reserved) bit 10 Undervoltage warning enable bit 11 Overvoltage warning enable bit 12 Underpower warning enable bit 13 Overpower warning enable bit 14 Under power factor warning enable bit 15 Over power factor warning enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 636 | 635 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 637 | 636 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 638 | 637 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 639 | 638 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 640 | 639 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 641 | 640 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 642 | 641 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 643 | 642 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 644 | 643 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 645 | 644 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 646 | 645 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 647 | 646 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 648 | 647 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 649 | 648 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 650 | 649 | 0x03,0x06,0x10 | N
Settings
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 651 | 650 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 652 | 651 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 653 | 652 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 654 | 653 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 655 | 654 | 0x03,0x06,0x10 | N
Date_time SS 00 (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 656 | 655 | 0x03,0x06,0x10 | Y
Date_time HH mm (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 657 | 656 | 0x03,0x06,0x10 | Y
Date_time MM DD (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 658 | 657 | 0x03,0x06,0x10 | Y
Date_time YY YY (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 659 | 658 | 0x03,0x06,0x10 | Y
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 660 | 659 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 80 | 40 |  |  |  |  | RW | 661 | 660 | 0x03,0x06,0x10 | N
Commands
Permissive Commands | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 701 | 700 | 0x03,0x06,0x10 | N | 0 |  | Bit 0: Permissive Command 1 Bit 1: Permissive Command 2 Bit 2: Permissive Command 3 Bit 3: Permissive Command 4 Bit 4: Permissive Command 5 Bit 5: Permissive Command 6 Bit 6: Permissive Command 7 Bit 7: Permissive Command 8 | 1
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 702 | 701 | 0x03,0x06,0x10 | N |  |  |  | 2
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 703 | 702 | 0x03,0x06,0x10 | N |  |  |  | 3
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 704 | 703 | 0x03,0x06,0x10 | N |  |  |  | 4
Command register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 705 | 704 | 0x03,0x06,0x10 | N |  |  | bit 0: Motor run forward / High speed forward command bit 1: Motor run reverse / High speed reverse command bit 2:Local/Remote Mode Sel 1 bit 3: Trip reset command bit 4: Local/Remote Mode Sel 2 bit 5: Self test (without trip) command bit 6: Motor low speed forward command bit 7: Motor low speed reverse command bit 8: Reset Inhibit command bit 9: Reset no of starts command bit 10: Reset no of stops command bit 11: Clear Energy command bit 12: Motor Stop command bit 13: Logic test command bit 14: Reset run hour command bit 15: Self test (with trip) command | 5
Command register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 706 | 705 | 0x03,0x06,0x10 | N |  |  | bit 0: Clear all command bit 1: Reserved bit 2: Clear thermal capacity level command bit 3: Clear controller settings command bit 4: Clear network port settings command bit 5: Clear Trip counter command bit 6: Factory reset command bit 7: Soft starter reset command bits 8-12: Reserved bit 13: Store reference start curve command bit 14: Clear trip records command bit 15: Clear event records command | 6
Reserved | UINT16 | 188 | 94 |  |  |  |  | RW | 707 | 706 | 0x03,0x06,0x10 | N |  |  |  | 7
User Map addresses
Parameter 1 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 801 | 800 | 0x03,0x06,0x10 | Y
Parameter 2 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 802 | 801 | 0x03,0x06,0x10 | Y
Parameter 3 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 803 | 802 | 0x03,0x06,0x10 | Y
Parameter 4 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 804 | 803 | 0x03,0x06,0x10 | Y
Parameter 5 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 805 | 804 | 0x03,0x06,0x10 | Y
Parameter 6 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 806 | 805 | 0x03,0x06,0x10 | Y
Parameter 7 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 807 | 806 | 0x03,0x06,0x10 | Y
Parameter 8 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 808 | 807 | 0x03,0x06,0x10 | Y
Parameter 9 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 809 | 808 | 0x03,0x06,0x10 | Y
Parameter 10 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 810 | 809 | 0x03,0x06,0x10 | Y
Parameter 11 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 811 | 810 | 0x03,0x06,0x10 | Y
Parameter 12 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 812 | 811 | 0x03,0x06,0x10 | Y
Parameter 13 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 813 | 812 | 0x03,0x06,0x10 | Y
Parameter 14 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 814 | 813 | 0x03,0x06,0x10 | Y
Parameter 15 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 815 | 814 | 0x03,0x06,0x10 | Y
Parameter 16 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 816 | 815 | 0x03,0x06,0x10 | Y
Parameter 17 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 817 | 816 | 0x03,0x06,0x10 | Y
Parameter 18 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 818 | 817 | 0x03,0x06,0x10 | Y
Parameter 19 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 819 | 818 | 0x03,0x06,0x10 | Y
Parameter 20 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 820 | 819 | 0x03,0x06,0x10 | Y
Parameter 21 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 821 | 820 | 0x03,0x06,0x10 | Y
Parameter 22 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 822 | 821 | 0x03,0x06,0x10 | Y
Parameter 23 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 823 | 822 | 0x03,0x06,0x10 | Y
Parameter 24 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 824 | 823 | 0x03,0x06,0x10 | Y
Parameter 25 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 825 | 824 | 0x03,0x06,0x10 | Y
Parameter 26 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 826 | 825 | 0x03,0x06,0x10 | Y
Parameter 27 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 827 | 826 | 0x03,0x06,0x10 | Y
Parameter 28 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 828 | 827 | 0x03,0x06,0x10 | Y
Parameter 29 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 829 | 828 | 0x03,0x06,0x10 | Y
Parameter 30 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 830 | 829 | 0x03,0x06,0x10 | Y
Parameter 31 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 831 | 830 | 0x03,0x06,0x10 | Y
Parameter 32 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 832 | 831 | 0x03,0x06,0x10 | Y
Parameter 33 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 833 | 832 | 0x03,0x06,0x10 | Y
Parameter 34 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 834 | 833 | 0x03,0x06,0x10 | Y
Parameter 35 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 835 | 834 | 0x03,0x06,0x10 | Y
Parameter 36 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 836 | 835 | 0x03,0x06,0x10 | Y
Parameter 37 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 837 | 836 | 0x03,0x06,0x10 | Y
Parameter 38 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 838 | 837 | 0x03,0x06,0x10 | Y
Parameter 39 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 839 | 838 | 0x03,0x06,0x10 | Y
Parameter 40 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 840 | 839 | 0x03,0x06,0x10 | Y
Parameter 41 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 841 | 840 | 0x03,0x06,0x10 | Y
Parameter 42 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 842 | 841 | 0x03,0x06,0x10 | Y
Parameter 43 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 843 | 842 | 0x03,0x06,0x10 | Y
Parameter 44 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 844 | 843 | 0x03,0x06,0x10 | Y
Parameter 45 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 845 | 844 | 0x03,0x06,0x10 | Y
Parameter 46 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 846 | 845 | 0x03,0x06,0x10 | Y
Parameter 47 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 847 | 846 | 0x03,0x06,0x10 | Y
Parameter 48 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 848 | 847 | 0x03,0x06,0x10 | Y
Parameter 49 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 849 | 848 | 0x03,0x06,0x10 | Y
Parameter 50 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 850 | 849 | 0x03,0x06,0x10 | Y
Parameter 51 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 851 | 850 | 0x03,0x06,0x10 | Y
Parameter 52 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 852 | 851 | 0x03,0x06,0x10 | Y
Parameter 53 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 853 | 852 | 0x03,0x06,0x10 | Y
Parameter 54 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 854 | 853 | 0x03,0x06,0x10 | Y
Parameter 55 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 855 | 854 | 0x03,0x06,0x10 | Y
Parameter 56 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 856 | 855 | 0x03,0x06,0x10 | Y
Parameter 57 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 857 | 856 | 0x03,0x06,0x10 | Y
Parameter 58 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 858 | 857 | 0x03,0x06,0x10 | Y
Parameter 59 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 859 | 858 | 0x03,0x06,0x10 | Y
Parameter 60 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 860 | 859 | 0x03,0x06,0x10 | Y
Parameter 61 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 861 | 860 | 0x03,0x06,0x10 | Y
Parameter 62 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 862 | 861 | 0x03,0x06,0x10 | Y
Parameter 63 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 863 | 862 | 0x03,0x06,0x10 | Y
Parameter 64 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 864 | 863 | 0x03,0x06,0x10 | Y
Parameter 65 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 865 | 864 | 0x03,0x06,0x10 | Y
Parameter 66 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 866 | 865 | 0x03,0x06,0x10 | Y
Parameter 67 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 867 | 866 | 0x03,0x06,0x10 | Y
Parameter 68 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 868 | 867 | 0x03,0x06,0x10 | Y
Parameter 69 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 869 | 868 | 0x03,0x06,0x10 | Y
Parameter 70 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 870 | 869 | 0x03,0x06,0x10 | Y
Parameter 71 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 871 | 870 | 0x03,0x06,0x10 | Y
Parameter 72 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 872 | 871 | 0x03,0x06,0x10 | Y
Parameter 73 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 873 | 872 | 0x03,0x06,0x10 | Y
Parameter 74 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 874 | 873 | 0x03,0x06,0x10 | Y
Parameter 75 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 875 | 874 | 0x03,0x06,0x10 | Y
Parameter 76 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 876 | 875 | 0x03,0x06,0x10 | Y
Parameter 77 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 877 | 876 | 0x03,0x06,0x10 | Y
Parameter 78 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 878 | 877 | 0x03,0x06,0x10 | Y
Parameter 79 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 879 | 878 | 0x03,0x06,0x10 | Y
Parameter 80 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 880 | 879 | 0x03,0x06,0x10 | Y
Parameter 81 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 881 | 880 | 0x03,0x06,0x10 | Y
Parameter 82 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 882 | 881 | 0x03,0x06,0x10 | Y
Parameter 83 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 883 | 882 | 0x03,0x06,0x10 | Y
Parameter 84 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 884 | 883 | 0x03,0x06,0x10 | Y
Parameter 85 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 885 | 884 | 0x03,0x06,0x10 | Y
Parameter 86 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 886 | 885 | 0x03,0x06,0x10 | Y
Parameter 87 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 887 | 886 | 0x03,0x06,0x10 | Y
Parameter 88 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 888 | 887 | 0x03,0x06,0x10 | Y
Parameter 89 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 889 | 888 | 0x03,0x06,0x10 | Y
Parameter 90 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 890 | 889 | 0x03,0x06,0x10 | Y
Parameter 91 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 891 | 890 | 0x03,0x06,0x10 | Y
Parameter 92 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 892 | 891 | 0x03,0x06,0x10 | Y
Parameter 93 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 893 | 892 | 0x03,0x06,0x10 | Y
Parameter 94 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 894 | 893 | 0x03,0x06,0x10 | Y
Parameter 95 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 895 | 894 | 0x03,0x06,0x10 | Y
Parameter 96 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 896 | 895 | 0x03,0x06,0x10 | Y
Parameter 97 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 897 | 896 | 0x03,0x06,0x10 | Y
Parameter 98 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 898 | 897 | 0x03,0x06,0x10 | Y
Parameter 99 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 899 | 898 | 0x03,0x06,0x10 | Y
Parameter 100 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 900 | 899 | 0x03,0x06,0x10 | Y
User Map values
Parameter 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 901 | 900 | 0x03,0x06,0x10 | N
Parameter 2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 902 | 901 | 0x03,0x06,0x10 | N
Parameter 3 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 903 | 902 | 0x03,0x06,0x10 | N
Parameter 4 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 904 | 903 | 0x03,0x06,0x10 | N
Parameter 5 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 905 | 904 | 0x03,0x06,0x10 | N
Parameter 6 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 906 | 905 | 0x03,0x06,0x10 | N
Parameter 7 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 907 | 906 | 0x03,0x06,0x10 | N
Parameter 8 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 908 | 907 | 0x03,0x06,0x10 | N
Parameter 9 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 909 | 908 | 0x03,0x06,0x10 | N
Parameter 10 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 910 | 909 | 0x03,0x06,0x10 | N
Parameter 11 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 911 | 910 | 0x03,0x06,0x10 | N
Parameter 12 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 912 | 911 | 0x03,0x06,0x10 | N
Parameter 13 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 913 | 912 | 0x03,0x06,0x10 | N
Parameter 14 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 914 | 913 | 0x03,0x06,0x10 | N
Parameter 15 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 915 | 914 | 0x03,0x06,0x10 | N
Parameter 16 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 916 | 915 | 0x03,0x06,0x10 | N
Parameter 17 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 917 | 916 | 0x03,0x06,0x10 | N
Parameter 18 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 918 | 917 | 0x03,0x06,0x10 | N
Parameter 19 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 919 | 918 | 0x03,0x06,0x10 | N
Parameter 20 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 920 | 919 | 0x03,0x06,0x10 | N
Parameter 21 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 921 | 920 | 0x03,0x06,0x10 | N
Parameter 22 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 922 | 921 | 0x03,0x06,0x10 | N
Parameter 23 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 923 | 922 | 0x03,0x06,0x10 | N
Parameter 24 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 924 | 923 | 0x03,0x06,0x10 | N
Parameter 25 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 925 | 924 | 0x03,0x06,0x10 | N
Parameter 26 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 926 | 925 | 0x03,0x06,0x10 | N
Parameter 27 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 927 | 926 | 0x03,0x06,0x10 | N
Parameter 28 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 928 | 927 | 0x03,0x06,0x10 | N
Parameter 29 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 929 | 928 | 0x03,0x06,0x10 | N
Parameter 30 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 930 | 929 | 0x03,0x06,0x10 | N
Parameter 31 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 931 | 930 | 0x03,0x06,0x10 | N
Parameter 32 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 932 | 931 | 0x03,0x06,0x10 | N
Parameter 33 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 933 | 932 | 0x03,0x06,0x10 | N
Parameter 34 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 934 | 933 | 0x03,0x06,0x10 | N
Parameter 35 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 935 | 934 | 0x03,0x06,0x10 | N
Parameter 36 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 936 | 935 | 0x03,0x06,0x10 | N
Parameter 37 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 937 | 936 | 0x03,0x06,0x10 | N
Parameter 38 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 938 | 937 | 0x03,0x06,0x10 | N
Parameter 39 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 939 | 938 | 0x03,0x06,0x10 | N
Parameter 40 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 940 | 939 | 0x03,0x06,0x10 | N
Parameter 41 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 941 | 940 | 0x03,0x06,0x10 | N
Parameter 42 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 942 | 941 | 0x03,0x06,0x10 | N
Parameter 43 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 943 | 942 | 0x03,0x06,0x10 | N
Parameter 44 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 944 | 943 | 0x03,0x06,0x10 | N
Parameter 45 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 945 | 944 | 0x03,0x06,0x10 | N
Parameter 46 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 946 | 945 | 0x03,0x06,0x10 | N
Parameter 47 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 947 | 946 | 0x03,0x06,0x10 | N
Parameter 48 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 948 | 947 | 0x03,0x06,0x10 | N
Parameter 49 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 949 | 948 | 0x03,0x06,0x10 | N
Parameter 50 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 950 | 949 | 0x03,0x06,0x10 | N
Parameter 51 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 951 | 950 | 0x03,0x06,0x10 | N
Parameter 52 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 952 | 951 | 0x03,0x06,0x10 | N
Parameter 53 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 953 | 952 | 0x03,0x06,0x10 | N
Parameter 54 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 954 | 953 | 0x03,0x06,0x10 | N
Parameter 55 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 955 | 954 | 0x03,0x06,0x10 | N
Parameter 56 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 956 | 955 | 0x03,0x06,0x10 | N
Parameter 57 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 957 | 956 | 0x03,0x06,0x10 | N
Parameter 58 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 958 | 957 | 0x03,0x06,0x10 | N
Parameter 59 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 959 | 958 | 0x03,0x06,0x10 | N
Parameter 60 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 960 | 959 | 0x03,0x06,0x10 | N
Parameter 61 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 961 | 960 | 0x03,0x06,0x10 | N
Parameter 62 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 962 | 961 | 0x03,0x06,0x10 | N
Parameter 63 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 963 | 962 | 0x03,0x06,0x10 | N
Parameter 64 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 964 | 963 | 0x03,0x06,0x10 | N
Parameter 65 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 965 | 964 | 0x03,0x06,0x10 | N
Parameter 66 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 966 | 965 | 0x03,0x06,0x10 | N
Parameter 67 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 967 | 966 | 0x03,0x06,0x10 | N
Parameter 68 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 968 | 967 | 0x03,0x06,0x10 | N
Parameter 69 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 969 | 968 | 0x03,0x06,0x10 | N
Parameter 70 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 970 | 969 | 0x03,0x06,0x10 | N
Parameter 71 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 971 | 970 | 0x03,0x06,0x10 | N
Parameter 72 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 972 | 971 | 0x03,0x06,0x10 | N
Parameter 73 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 973 | 972 | 0x03,0x06,0x10 | N
Parameter 74 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 974 | 973 | 0x03,0x06,0x10 | N
Parameter 75 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 975 | 974 | 0x03,0x06,0x10 | N
Parameter 76 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 976 | 975 | 0x03,0x06,0x10 | N
Parameter 77 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 977 | 976 | 0x03,0x06,0x10 | N
Parameter 78 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 978 | 977 | 0x03,0x06,0x10 | N
Parameter 79 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 979 | 978 | 0x03,0x06,0x10 | N
Parameter 80 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 980 | 979 | 0x03,0x06,0x10 | N
Parameter 81 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 981 | 980 | 0x03,0x06,0x10 | N
Parameter 82 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 982 | 981 | 0x03,0x06,0x10 | N
Parameter 83 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 983 | 982 | 0x03,0x06,0x10 | N
Parameter 84 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 984 | 983 | 0x03,0x06,0x10 | N
Parameter 85 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 985 | 984 | 0x03,0x06,0x10 | N
Parameter 86 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 986 | 985 | 0x03,0x06,0x10 | N
Parameter 87 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 987 | 986 | 0x03,0x06,0x10 | N
Parameter 88 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 988 | 987 | 0x03,0x06,0x10 | N
Parameter 89 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 989 | 988 | 0x03,0x06,0x10 | N
Parameter 90 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 990 | 989 | 0x03,0x06,0x10 | N
Parameter 91 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 991 | 990 | 0x03,0x06,0x10 | N
Parameter 92 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 992 | 991 | 0x03,0x06,0x10 | N
Parameter 93 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 993 | 992 | 0x03,0x06,0x10 | N
Parameter 94 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 994 | 993 | 0x03,0x06,0x10 | N
Parameter 95 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 995 | 994 | 0x03,0x06,0x10 | N
Parameter 96 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 996 | 995 | 0x03,0x06,0x10 | N
Parameter 97 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 997 | 996 | 0x03,0x06,0x10 | N
Parameter 98 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 998 | 997 | 0x03,0x06,0x10 | N
Parameter 99 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 999 | 998 | 0x03,0x06,0x10 | N
Parameter 100 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1000 | 999 | 0x03,0x06,0x10 | N
HMI registers
Reserved | UINT16 | 40 | 20 | 0 | 65535 | 1 | 1 | R | 1001 | 1000 | 0x03 | N
HMI Keys (Programmable) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1021 | 1020 | 0x03 | N
Reserved | UINT16 | 358 | 179 | 0 | 65535 | 1 | 1 | R | 1022 | 1021 | 0x03 | N
Custom Logic Variables
Custom logic status register | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1201 | 1200 | 0x03 | N
Custom logic version | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1202 | 1201 | 0x03 | N
Custom logic memory space | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1203 | 1202 | 0x03 | N
Custom logic memory used | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1204 | 1203 | 0x03 | N
Custom logic temporary space | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1205 | 1204 | 0x03 | N
Custom logic non-volatile space | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1206 | 1205 | 0x03 | N
Reserved | UINT16 | 88 | 44 | 0 | 0 | 1 | 1 | R | 1207 | 1206 | 0x03 | N
Custom logic setting register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1251 | 1250 | 0x03,0x06,0x10 | Y
Reserved | UINT16 | 38 | 19 | 0 | 0 | 1 | 1 | RW | 1252 | 1251 | 0x03,0x06,0x10 | N
Custom logic command register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1271 | 1270 | 0x03,0x06,0x10 | Y
Reserved | UINT16 | 18 | 9 | 0 | 0 | 1 | 1 | RW | 1272 | 1271 | 0x03,0x06,0x10 | N
Custom logic monitoring register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1281 | 1280 | 0x03 | N
Reserved | UINT16 | 20 | 10 | 0 | 0 | 1 | 1 | R | 1282 | 1281 | 0x03 | N
TesysTera CL DO Input Information | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1292 | 1291 | 0x03 | N |  |  | Bit 0:CL DO1 Input information Bit 1:CL DO2 Input information Bit 2:CL DO3 Input information Bit 3:CL DO4 Input information Bit 4:CL DO5 Input information Bit 5:CL DO6 Input information Bit 6:CL DO7 Input information Bit 7:CL DO8 Input information Bit 8:CL DO9 Input information Bit 9:CL DO10 Input information Bit 10:CL DO11 Input information Bit 11:CL DO12 Input information Bit 12:CL DO13 Input information Bit 13:NA Bit 14:NA Bit 15:NA
Reserved | UINT16 | 18 | 9 | 0 | 65535 | 1 | 1 | R | 1293 | 1292 | 0x03 | N
Custom logic general purpose register1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1302 | 1301 | 0x03,0x06,0x10 | N
Custom logic general purpose register2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1303 | 1302 | 0x03,0x06,0x10 | N
Custom logic general purpose register3 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1304 | 1303 | 0x03,0x06,0x10 | N
Custom logic general purpose register4 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1305 | 1304 | 0x03,0x06,0x10 | N
Custom logic general purpose register5 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1306 | 1305 | 0x03,0x06,0x10 | N
Custom logic general purpose register6 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1307 | 1306 | 0x03,0x06,0x10 | N
Custom logic general purpose register7 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1308 | 1307 | 0x03,0x06,0x10 | N
Custom logic general purpose register8 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1309 | 1308 | 0x03,0x06,0x10 | N
Custom logic general purpose register9 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1310 | 1309 | 0x03,0x06,0x10 | N
Custom logic general purpose register10 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1311 | 1310 | 0x03,0x06,0x10 | N
Custom logic general purpose register11 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1312 | 1311 | 0x03,0x06,0x10 | N
Custom logic general purpose register12 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1313 | 1312 | 0x03,0x06,0x10 | N
Custom logic general purpose register13 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1314 | 1313 | 0x03,0x06,0x10 | N
Custom logic general purpose register14 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1315 | 1314 | 0x03,0x06,0x10 | N
Custom logic general purpose register15 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1316 | 1315 | 0x03,0x06,0x10 | N
Custom logic general purpose register16 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1317 | 1316 | 0x03,0x06,0x10 | N
Custom logic general purpose register17 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1318 | 1317 | 0x03,0x06,0x10 | N
Custom logic general purpose register18 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1319 | 1318 | 0x03,0x06,0x10 | N
Custom logic general purpose register19 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1320 | 1319 | 0x03,0x06,0x10 | N
Custom logic general purpose register20 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1321 | 1320 | 0x03,0x06,0x10 | N
Custom logic general purpose register21 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1322 | 1321 | 0x03,0x06,0x10 | N
Custom logic general purpose register22 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1323 | 1322 | 0x03,0x06,0x10 | N
Custom logic general purpose register23 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1324 | 1323 | 0x03,0x06,0x10 | N
Custom logic general purpose register24 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1325 | 1324 | 0x03,0x06,0x10 | N
Custom logic general purpose register25 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1326 | 1325 | 0x03,0x06,0x10 | N
Custom logic general purpose register26 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1327 | 1326 | 0x03,0x06,0x10 | N
Custom logic general purpose register27 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1328 | 1327 | 0x03,0x06,0x10 | N
Custom logic general purpose register28 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1329 | 1328 | 0x03,0x06,0x10 | N
Custom logic general purpose register29 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1330 | 1329 | 0x03,0x06,0x10 | N
Custom logic general purpose register30 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1331 | 1330 | 0x03,0x06,0x10 | N
Custom logic general purpose register31 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1332 | 1331 | 0x03,0x06,0x10 | N
Custom logic general purpose register32 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1333 | 1332 | 0x03,0x06,0x10 | N
Custom logic general purpose register33 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1334 | 1333 | 0x03,0x06,0x10 | N
Custom logic general purpose register34 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1335 | 1334 | 0x03,0x06,0x10 | N
Custom logic general purpose register35 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1336 | 1335 | 0x03,0x06,0x10 | N
Custom logic general purpose register36 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1337 | 1336 | 0x03,0x06,0x10 | N
Custom logic general purpose register37 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1338 | 1337 | 0x03,0x06,0x10 | N
Custom logic general purpose register38 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1339 | 1338 | 0x03,0x06,0x10 | N
Custom logic general purpose register39 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1340 | 1339 | 0x03,0x06,0x10 | N
Custom logic general purpose register40 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1341 | 1340 | 0x03,0x06,0x10 | N
Custom logic general purpose register41 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1342 | 1341 | 0x03,0x06,0x10 | N
Custom logic general purpose register42 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1343 | 1342 | 0x03,0x06,0x10 | N
Custom logic general purpose register43 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1344 | 1343 | 0x03,0x06,0x10 | N
Custom logic general purpose register44 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1345 | 1344 | 0x03,0x06,0x10 | N
Custom logic general purpose register45 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1346 | 1345 | 0x03,0x06,0x10 | N
Custom logic general purpose register46 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1347 | 1346 | 0x03,0x06,0x10 | N
Custom logic general purpose register47 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1348 | 1347 | 0x03,0x06,0x10 | N
Custom logic general purpose register48 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1349 | 1348 | 0x03,0x06,0x10 | N
Custom logic general purpose register49 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1350 | 1349 | 0x03,0x06,0x10 | N
Custom logic general purpose register50 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1351 | 1350 | 0x03,0x06,0x10 | N
Custom logic general purpose register51 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1352 | 1351 | 0x03,0x06,0x10 | N
Custom logic general purpose register52 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1353 | 1352 | 0x03,0x06,0x10 | N
Custom logic general purpose register53 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1354 | 1353 | 0x03,0x06,0x10 | N
Custom logic general purpose register54 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1355 | 1354 | 0x03,0x06,0x10 | N
Custom logic general purpose register55 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1356 | 1355 | 0x03,0x06,0x10 | N
Custom logic general purpose register56 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1357 | 1356 | 0x03,0x06,0x10 | N
Custom logic general purpose register57 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1358 | 1357 | 0x03,0x06,0x10 | N
Custom logic general purpose register58 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1359 | 1358 | 0x03,0x06,0x10 | N
Custom logic general purpose register59 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1360 | 1359 | 0x03,0x06,0x10 | N
Custom logic general purpose register60 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1361 | 1360 | 0x03,0x06,0x10 | N
Custom logic general purpose register61 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1362 | 1361 | 0x03,0x06,0x10 | N
Custom logic general purpose register62 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1363 | 1362 | 0x03,0x06,0x10 | N
Custom logic general purpose register63 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1364 | 1363 | 0x03,0x06,0x10 | N
Custom logic general purpose register64 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1365 | 1364 | 0x03,0x06,0x10 | N
Custom logic general purpose register65 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1366 | 1365 | 0x03,0x06,0x10 | N
Custom logic general purpose register66 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1367 | 1366 | 0x03,0x06,0x10 | N
Custom logic general purpose register67 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1368 | 1367 | 0x03,0x06,0x10 | N
Custom logic general purpose register68 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1369 | 1368 | 0x03,0x06,0x10 | N
Custom logic general purpose register69 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1370 | 1369 | 0x03,0x06,0x10 | N
Custom logic general purpose register70 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1371 | 1370 | 0x03,0x06,0x10 | N
Custom logic general purpose register71 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1372 | 1371 | 0x03,0x06,0x10 | N
Custom logic general purpose register72 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1373 | 1372 | 0x03,0x06,0x10 | N
Custom logic general purpose register73 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1374 | 1373 | 0x03,0x06,0x10 | N
Custom logic general purpose register74 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1375 | 1374 | 0x03,0x06,0x10 | N
Custom logic general purpose register75 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1376 | 1375 | 0x03,0x06,0x10 | N
Custom logic general purpose register76 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1377 | 1376 | 0x03,0x06,0x10 | N
Custom logic general purpose register77 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1378 | 1377 | 0x03,0x06,0x10 | N
Custom logic general purpose register78 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1379 | 1378 | 0x03,0x06,0x10 | N
Custom logic general purpose register79 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1380 | 1379 | 0x03,0x06,0x10 | N
Custom logic general purpose register80 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1381 | 1380 | 0x03,0x06,0x10 | N
Custom logic general purpose register81 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1382 | 1381 | 0x03,0x06,0x10 | N
Custom logic general purpose register82 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1383 | 1382 | 0x03,0x06,0x10 | N
Custom logic general purpose register83 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1384 | 1383 | 0x03,0x06,0x10 | N
Custom logic general purpose register84 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1385 | 1384 | 0x03,0x06,0x10 | N
Custom logic general purpose register85 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1386 | 1385 | 0x03,0x06,0x10 | N
Custom logic general purpose register86 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1387 | 1386 | 0x03,0x06,0x10 | N
Custom logic general purpose register87 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1388 | 1387 | 0x03,0x06,0x10 | N
Custom logic general purpose register88 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1389 | 1388 | 0x03,0x06,0x10 | N
Custom logic general purpose register89 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1390 | 1389 | 0x03,0x06,0x10 | N
Custom logic general purpose register90 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1391 | 1390 | 0x03,0x06,0x10 | N
Custom logic general purpose register91 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1392 | 1391 | 0x03,0x06,0x10 | N
Custom logic general purpose register92 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1393 | 1392 | 0x03,0x06,0x10 | N
Custom logic general purpose register93 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1394 | 1393 | 0x03,0x06,0x10 | N
Custom logic general purpose register94 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1395 | 1394 | 0x03,0x06,0x10 | N
Custom logic general purpose register95 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1396 | 1395 | 0x03,0x06,0x10 | N
Custom logic general purpose register96 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1397 | 1396 | 0x03,0x06,0x10 | N
Custom logic general purpose register97 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1398 | 1397 | 0x03,0x06,0x10 | N
Custom logic general purpose register98 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1399 | 1398 | 0x03,0x06,0x10 | N
Custom logic general purpose register99 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1400 | 1399 | 0x03,0x06,0x10 | N
Only applicable for Modbus/TCP and EIP
Mirroring Variables
[15 empty] | 140->01-> | 8C->01->
Mirror register 1: Not applicable | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2501 | 2500 | 0x03 | N |  |  | 1 | 1
Mirror register 2: Not applicable | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2502 | 2501 | 0x03 | N |  |  | 2 | 2
System Status register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2503 | 2502 | 0x03 | N |  |  | 3 | 3
System Status register 2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2504 | 2503 | 0x03 | N |  |  | 4 | 4
Logic Input status register | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2505 | 2504 | 0x03 | N |  |  | 5 | 5
Logic Output status register | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2506 | 2505 | 0x03 | N |  |  | 6 | 6
Permissive Commands | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R/W | 2507 | 2506 | 0x03,0x06,0x10 | N |  |  | 7 | 7 | Bit 0: Permissive Command 1 Bit 1: Permissive Command 2 Bit 2: Permissive Command 3 Bit 3: Permissive Command 4 Bit 4: Permissive Command 5 Bit 5: Permissive Command 6 Bit 6: Permissive Command 7 Bit 7: Permissive Command 8
Command Register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R/W | 2508 | 2507 | 0x03,0x06,0x10 | N |  |  | 8 | 8 | bit 0: Motor run forward / High speed forward command bit 1: Motor run reverse / High speed reverse command bit 2:Local/Remote Mode Sel 1 bit 3: Trip reset command bit 4: Local/Remote Mode Sel 2 bit 5: Self test (without trip) command bit 6: Motor low speed forward command bit 7: Motor low speed reverse command bit 8: Reset Inhibit command bit 9: Reset no of starts command bit 10: Reset no of stops command bit 11: Clear Energy command bit 12: Motor Stop command bit 13: Logic test command bit 14: Reset run hour command bit 15: Self test (with trip) command
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R/W | 2509 | 2508 | 0x03,0x06,0x10 | N |  |  | 9 | 9
Table 1
Last trip statistics Register | Trip n-1 statistics Register | Trip n-2 statistics Register | Trip n-3 statistics Register | Trip n-4 statistics Register | Variable Type | Read-only Variables
150 | 180 | 210 | 240 | 270 | UINT16 | Trip code
151 | 181 | 211 | 241 | 271 | UINT16 | Motor full load current ratio (% FLC max)
152 | 182 | 212 | 242 | 272 | UINT16 | Thermal capacity level (% trip level)
153 | 183 | 213 | 243 | 273 | UINT16 | Average current ratio (% FLC)
154 | 184 | 214 | 244 | 274 | UINT16 | L1 current ratio (% FLC)
155 | 185 | 215 | 245 | 275 | UINT16 | L2 current ratio (% FLC)
156 | 186 | 216 | 246 | 276 | UINT16 | L3 current ratio (% FLC)
157 | 187 | 217 | 247 | 277 | UINT16 | Ground current ratio (x 0.1 % FLC min)
158 | 188 | 218 | 248 | 278 | UINT16 | Full load current max (x 0.1 A)
159 | 189 | 219 | 249 | 279 | UINT16 | Current phase imbalance (%)
160 | 190 | 220 | 250 | 280 | UINT16 | Frequency (x 0.1 Hz)
161 | 191 | 221 | 251 | 281 | UINT16 | Motor temperature sensor (x 0.1 Ω)
162-165 | 192-195 | 222-225 | 252-255 | 282-285 | UINT16 (4) | DateTime
166 | 196 | 226 | 256 | 286 | UINT16 | Average voltage (V)
167 | 197 | 227 | 257 | 287 | UINT16 | L3-L1 voltage (V)
168 | 198 | 228 | 258 | 288 | UINT16 | L1-L2 voltage (V)
169 | 199 | 229 | 259 | 289 | UINT16 | L2-L3 voltage (V)
170 | 200 | 230 | 260 | 290 | UINT16 | Voltage phase imbalance (%)
171 | 201 | 231 | 261 | 291 | UINT16 | Active power (x 0.1 kW)
172 | 202 | 232 | 262 | 292 | UINT16 | Power factor (x 0.01)
173-179 | 203-209 | 233-239 | 263-269 | 293-299 | UINT16 | Reserved
Table 2
Last trip extention Register | Trip n-1 extention Register | Trip n-2 extention Register | Trip n-3 extention Register | Trip n-4 extention Register | Variable Type | Read-only Variables
300-301 | 330-331 | 360-361 | 390-391 | 420-421 | UINT32 | Average current (x 0.01 A)
302-303 | 332-333 | 362-363 | 392-393 | 422-423 | UINT32 | L1 current (x 0.01 A)
304-305 | 334-335 | 364-365 | 394-395 | 424-425 | UINT32 | L2 current (x 0.01 A)
306-307 | 336-337 | 366-367 | 396-397 | 426-427 | UINT32 | L3 current (x 0.01 A)
308-309 | 338-339 | 368-369 | 398-399 | 428-429 | UINT32 | Ground current (mA)
310 | 340 | 370 | 400 | 430 | UINT16 | Motor temperature sensor degree (°C)

## TeSys T Parameters_old (hidden)
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Global Statistics
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 101 | 100 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 102 | 101 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 103 | 102 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 104 | 103 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 105 | 104 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 106 | 105 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 107 | 106 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 108 | 107 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 109 | 108 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 110 | 109 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 111 | 110 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 112 | 111 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 113 | 112 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 114 | 113 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 115 | 114 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 116 | 115 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 117 | 116 | 0x03 | N
Motor starts count | UINT32 | 4 | 2 |  |  |  |  | R | 118 | 117 | 0x03 | N
Motor Operating time | UINT32 | 4 | 2 |  |  |  |  | R | 120 | 119 | 0x03 | N
reserved | UINT16 | 2 | 1 |  |  |  |  | R | 122 | 121 | 0x03 | N
LTM monitoring Statistics
Trip Count | UINT16 | 2 | 1 |  |  |  |  | R | 123 | 122 | 0x03 | N
Alarm Count | UINT16 | 2 | 1 |  |  |  |  | R | 124 | 123 | 0x03 | N
Motor LO1 Closing count | UINT32 | 4 | 2 |  |  |  |  | R | 125 | 124 | 0x03 | N
Motor LO2 Closing count | UINT32 | 4 | 2 |  |  |  |  | R | 127 | 126 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 129 | 128 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 130 | 129 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 131 | 130 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 132 | 131 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 133 | 132 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 134 | 133 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 135 | 134 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 136 | 135 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 137 | 136 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 138 | 137 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 139 | 138 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 140 | 139 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 141 | 140 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 142 | 141 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 143 | 142 | 0x03 | N
Active Power Consumption | UINT32 | 4 | 2 |  |  |  |  | R | 144 | 143 | 0x03 | N
Reactive Power Consumption | UINT32 | 4 | 2 |  |  |  |  | R | 146 | 145 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 148 | 147 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 149 | 148 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 150 | 149 | 0x03 | N
Trip statistics
Last trip statistics | UINT16 | 60 | 30 |  |  |  |  | R | 151 | 150 | 0x03 | N
Trip n-1 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 181 | 180 | 0x03 | N
Trip n-2 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 211 | 210 | 0x03 | N
Trip n-3 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 241 | 240 | 0x03 | N
Trip n-4 statistics | UINT16 | 60 | 30 |  |  |  |  | R | 271 | 270 | 0x03 | N
trip statistics - Extention
Last trip extention | UINT16 | 60 | 30 |  |  |  |  | R | 301 | 300 | 0x03 | N
Trip n-1 extention | UINT16 | 60 | 30 |  |  |  |  | R | 331 | 330 | 0x03 | N
Trip n-2 extention | UINT16 | 60 | 30 |  |  |  |  | R | 361 | 360 | 0x03 | N
Trip n-3 extention | UINT16 | 60 | 30 |  |  |  |  | R | 391 | 390 | 0x03 | N
Trip n-4 extention | UINT16 | 60 | 30 |  |  |  |  | R | 421 | 420 | 0x03 | N
Monitoring Variables
Minimum wait time | UINT16 | 2 | 1 |  |  |  |  | R | 451 | 450 | 0x03 | N
Trip code | UINT16 | 2 | 1 |  |  |  |  | R | 452 | 451 | 0x03 | N
Trip register 1 | BITMAP | 2 | 1 |  |  |  |  | R | 453 | 452 | 0x03 | N
Trip register 2 | BITMAP | 2 | 1 |  |  |  |  | R | 454 | 453 | 0x03 | N
Trip register 3 | BITMAP | 2 | 1 |  |  |  |  | R | 455 | 454 | 0x03 | N
System Status register 1 | BITMAP | 2 | 1 |  |  |  |  | R | 456 | 455 | 0x03 | N |  |  | bit 1 System on bit 2 System fault bit 3 System warning bit 4 System tripped bit 5 Fault reset authorized bit 6 Controller power bit 7 Motor running (with detection of a current, if greater than 10% FLC) bits 8-13 Motor average current ratio 32 = 100% FLC - 63 = 200% FLC bit 14 In remote bit 15 Motor starting (start in progress) 0 = descending current is less than 150% FLC 1 = ascending current is greater than 10% FLC
System Status register 2 | BITMAP | 2 | 1 |  |  |  |  | R | 457 | 456 | 0x03 | N |  |  | bit 0 Auto-reset active bit 1 (Not significant) bit 2 Fault power cycle requested bit 3 Motor restart time undefined bit 4 Rapid cycle lockout bit 5 Load shedding bit 6 Motor speed 0 = FLC1 setting is used 1 = FLC2 setting is used bit 7 HMI port comm loss bit 8 Network port comm loss bit 9 Motor transition lockout bits 10-15 (Not significant)
Logic Input status register | BITMAP | 2 | 1 |  |  |  |  | R | 458 | 457 | 0x03 | N
Logic Output status register | BITMAP | 2 | 1 |  |  |  |  | R | 459 | 458 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 460 | 459 | 0x03 | N
Alarm Code | UINT16 | 2 | 1 |  |  |  |  | R | 461 | 460 | 0x03 | N
Alarm Register 1 | BITMAP | 2 | 1 |  |  |  |  | R | 462 | 461 | 0x03 | N
Alarm Register 2 | BITMAP | 2 | 1 |  |  |  |  | R | 463 | 462 | 0x03 | N
Alarm Register 3 | BITMAP | 2 | 1 |  |  |  |  | R | 464 | 463 | 0x03 | N
Motor Temperature sensor degree | UINT16 | 2 | 1 |  |  |  |  | R | 465 | 464 | 0x03 | N
Thermal capacity level | UINT16 | 2 | 1 |  |  |  |  | R | 466 | 465 | 0x03 | N
Average current ratio | UINT16 | 2 | 1 |  |  |  |  | R | 467 | 466 | 0x03 | N
L1 Current ratio | UINT16 | 2 | 1 |  |  |  |  | R | 468 | 467 | 0x03 | N
L2 Current ratio | UINT16 | 2 | 1 |  |  |  |  | R | 469 | 468 | 0x03 | N
L3 Current ratio | UINT16 | 2 | 1 |  |  |  |  | R | 470 | 469 | 0x03 | N
Ground Current Ratio | UINT16 | 2 | 1 |  |  |  |  | R | 471 | 470 | 0x03 | N
Current Phase Imbalance | UINT16 | 2 | 1 |  |  |  |  | R | 472 | 471 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 473 | 472 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 474 | 473 | 0x03 | N
Frequency | UINT16 | 2 | 1 |  |  |  |  | R | 475 | 474 | 0x03 | N
Motor Temperature Sensor Ohm | UINT16 | 2 | 1 |  |  |  |  | R | 476 | 475 | 0x03 | N
Average Voltage | UINT16 | 2 | 1 |  |  |  |  | R | 477 | 476 | 0x03 | N
L3-L1 Voltage | UINT16 | 2 | 1 |  |  |  |  | R | 478 | 477 | 0x03 | N
L1-L2 Voltage | UINT16 | 2 | 1 |  |  |  |  | R | 479 | 478 | 0x03 | N
L2-L3 Voltage | UINT16 | 2 | 1 |  |  |  |  | R | 480 | 479 | 0x03 | N
Voltage Phase Imbalance | UINT16 | 2 | 1 |  |  |  |  | R | 481 | 480 | 0x03 | N
Power Factor | UINT16 | 2 | 1 |  |  |  |  | R | 482 | 481 | 0x03 | N
Active Power | UINT16 | 2 | 1 |  |  |  |  | R | 483 | 482 | 0x03 | N
Reactive Power | UINT16 | 2 | 1 |  |  |  |  | R | 484 | 483 | 0x03 | N
Auto Restart Status Register | BITMAP | 2 | 1 |  |  |  |  | R | 485 | 484 | 0x03 | N
Controller Last PowerOff Duration | UINT16 | 2 | 1 |  |  |  |  | R | 486 | 485 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 487 | 486 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 488 | 487 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 489 | 488 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 490 | 489 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 491 | 490 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 492 | 491 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 493 | 492 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 494 | 493 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 495 | 494 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 496 | 495 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 497 | 496 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 498 | 497 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 499 | 498 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 500 | 499 | 0x03 | N
Average Current | UINT32 | 4 | 2 |  |  |  |  | R | 501 | 500 | 0x03 | N
L1 Current | UINT32 | 4 | 2 |  |  |  |  | R | 503 | 502 | 0x03 | N
L2 Current | UINT32 | 4 | 2 |  |  |  |  | R | 505 | 504 | 0x03 | N
L3 Current | UINT32 | 4 | 2 |  |  |  |  | R | 507 | 506 | 0x03 | N
Ground Current | UINT32 | 4 | 2 |  |  |  |  | R | 509 | 508 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 511 | 510 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 512 | 511 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 513 | 512 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 514 | 513 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 515 | 514 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 516 | 515 | 0x03 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | R | 517 | 516 | 0x03 | N
Reserved | UINT16 | 46 | 23 |  |  |  |  | R | 518 | 517 | 0x03 | N
Configuration variables
Reserved | UINT16 | 122 | 61 | 0 | 0 | 0 | 0 | RW | 541 | 540 | 0x03,0x06,0x10 | N
General configuration register 1 | BITMAP | 2 | 1 | 0 | 1 | 1 | 1 | RW | 602 | 601 | 0x03,0x06,0x10 | Y | 0 |  | bit 0 Controller system config required 0 = exit the configuration menu 1 = go to the configuration menu
General configuration register 2 | BITMAP | 2 | 1 | 0 | 2048 | 2048 | 1 | RW | 603 | 602 | 0x03,0x06,0x10 | Y | 0 |  | bits 0-10(Reserved) bit 11: HMI motor status LED color 0: Red 1:Green bits 12-15 (Reserved)
Reserved | UINT16 | 56 | 28 | 0 | 0 | 0 | 0 | RW | 604 | 603 | 0x03,0x06,0x10
Trip enable register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 632 | 631 | 0x03,0x06,0x10 | Y |  |  | bits 0-1 (Reserved) bit 2 Calculated ground trip fault enable bit 3 Thermal overload fault enable bit 4 Long start fault enable bit 5 Stalled Rotor fault enable bit 6 Current phase imbalance fault enable bit 7 Undercurrent fault enable bit 8 (Reserved) bit 9 Self test enable 0 = disable 1 = enable (factory setting) bit 10 HMI port fault enable bits 11-14 (Reserved) bit 15 Network port fault enable
Alarm enable register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 633 | 632 | 0x03,0x06,0x10 | Y |  |  | bit 0 (Not significant) bit 1 (Reserved) bit 2 Calculated ground trip warning enable bit 3 Thermal overload warning enable bit 4 (Reserved) bit 5 Stalled Rotor warning enable bit 6 Current phase imbalance warning enable bit 7 Undercurrent warning enable bits 8- 9 (Reserved) bit 10 HMI port warning enable bit 11 Controller internal temperature warning enable bits 12-14 (Reserved) bit 15 Network port warning enable
Trip enable register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 634 | 633 | 0x03,0x06,0x10 | Y |  |  | bit 0 (Reserved) bit 1 Diagnostic fault enable bit 2 Wiring fault enable bit 3 Overcurrent fault enable bit 4 Current Phase loss fault enable bit 5 Current Phase reversal fault enable bit 6 Temperature (Main Unit) fault enable bit 7 Voltage imbalance fault enable bit 8 Voltage+Q130 phase loss fault enable bit 9 Voltage phase reversal fault enable bit 10 Undervoltage fault enable bit 11 Overvoltage fault enable bit 12 Underpower fault enable bit 13 Overpower fault enable bit 14 Under power factor fault enable bit 15 Over power factor fault enable
Alarm enable register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 635 | 634 | 0x03,0x06,0x10 | Y |  |  | bit 0 (Reserved) bit 1 Diagnostic warning enable bit 2 (Reserved) bit 3 Overcurrent warning enable bit 4 Current Phase loss warning enable bit 5 (Reserved) bit 6 Temperature (Main Unit) warning enable bit 7 Voltage imbalance warning enable bit 8 Voltage phase loss warning enable bit 9 (Reserved) bit 10 Undervoltage warning enable bit 11 Overvoltage warning enable bit 12 Underpower warning enable bit 13 Overpower warning enable bit 14 Under power factor warning enable bit 15 Over power factor warning enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 636 | 635 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 637 | 636 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 638 | 637 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 639 | 638 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 640 | 639 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 641 | 640 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 642 | 641 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 643 | 642 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 644 | 643 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 645 | 644 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 646 | 645 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 647 | 646 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 648 | 647 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 649 | 648 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 650 | 649 | 0x03,0x06,0x10 | N
Settings
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 651 | 650 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 652 | 651 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 653 | 652 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 654 | 653 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 655 | 654 | 0x03,0x06,0x10 | N
Date_time SS 00 (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 656 | 655 | 0x03,0x06,0x10 | Y
Date_time HH mm (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 657 | 656 | 0x03,0x06,0x10 | Y
Date_time MM DD (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 658 | 657 | 0x03,0x06,0x10 | Y
Date_time YY YY (BCD) | UINT16 | 2 | 1 |  |  |  |  | RW | 659 | 658 | 0x03,0x06,0x10 | Y
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 660 | 659 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 80 | 40 |  |  |  |  | RW | 661 | 660 | 0x03,0x06,0x10 | N
Commands
Permissive Commands | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 701 | 700 | 0x03,0x06,0x10 | N | 0 |  | Bit 0: Permissive Command 1 Bit 1: Permissive Command 2 Bit 2: Permissive Command 3 Bit 3: Permissive Command 4 Bit 4: Permissive Command 5 Bit 5: Permissive Command 6 Bit 6: Permissive Command 7 Bit 7: Permissive Command 8
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 702 | 701 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 703 | 702 | 0x03,0x06,0x10 | N
Reserved | UINT16 | 2 | 1 |  |  |  |  | RW | 704 | 703 | 0x03,0x06,0x10 | N
Command register 1 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 705 | 704 | 0x03,0x06,0x10 | N |  |  | bit 0: Motor run forward / High speed forward command bit 1: Motor run reverse / High speed reverse command bit 2:Local/Remote Mode Sel 1 bit 3: Trip reset command bit 4: Local/Remote Mode Sel 2 bit 5: Self test (without trip) command bit 6: Motor low speed forward command bit 7: Motor low speed reverse command bit 8: Reset Inhibit command bit 9: Reset no of starts command bit 10: Reset no of stops command bit 11: Clear Energy command bit 12: Motor Stop command bit 13: Logic test command bit 14: Reset run hour command bit 15: Self test (with trip) command
Command register 2 | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 706 | 705 | 0x03,0x06,0x10 | N |  |  | bit 0: Clear all command bit 1: Reserved bit 2: Clear thermal capacity level command bit 3: Clear controller settings command bit 4: Clear network port settings command bit 5: Clear Trip counter command bit 6: Factory reset command bit 7: Soft starter reset command bits 8-12: Reserved bit 13: Store reference start curve command bit 14: Clear trip records command bit 15: Clear event records command
Reserved | UINT16 | 188 | 94 |  |  |  |  | RW | 707 | 706 | 0x03,0x06,0x10 | N
User Map addresses
Parameter 1 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 801 | 800 | 0x03,0x06,0x10 | Y
Parameter 2 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 802 | 801 | 0x03,0x06,0x10 | Y
Parameter 3 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 803 | 802 | 0x03,0x06,0x10 | Y
Parameter 4 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 804 | 803 | 0x03,0x06,0x10 | Y
Parameter 5 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 805 | 804 | 0x03,0x06,0x10 | Y
Parameter 6 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 806 | 805 | 0x03,0x06,0x10 | Y
Parameter 7 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 807 | 806 | 0x03,0x06,0x10 | Y
Parameter 8 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 808 | 807 | 0x03,0x06,0x10 | Y
Parameter 9 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 809 | 808 | 0x03,0x06,0x10 | Y
Parameter 10 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 810 | 809 | 0x03,0x06,0x10 | Y
Parameter 11 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 811 | 810 | 0x03,0x06,0x10 | Y
Parameter 12 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 812 | 811 | 0x03,0x06,0x10 | Y
Parameter 13 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 813 | 812 | 0x03,0x06,0x10 | Y
Parameter 14 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 814 | 813 | 0x03,0x06,0x10 | Y
Parameter 15 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 815 | 814 | 0x03,0x06,0x10 | Y
Parameter 16 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 816 | 815 | 0x03,0x06,0x10 | Y
Parameter 17 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 817 | 816 | 0x03,0x06,0x10 | Y
Parameter 18 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 818 | 817 | 0x03,0x06,0x10 | Y
Parameter 19 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 819 | 818 | 0x03,0x06,0x10 | Y
Parameter 20 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 820 | 819 | 0x03,0x06,0x10 | Y
Parameter 21 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 821 | 820 | 0x03,0x06,0x10 | Y
Parameter 22 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 822 | 821 | 0x03,0x06,0x10 | Y
Parameter 23 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 823 | 822 | 0x03,0x06,0x10 | Y
Parameter 24 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 824 | 823 | 0x03,0x06,0x10 | Y
Parameter 25 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 825 | 824 | 0x03,0x06,0x10 | Y
Parameter 26 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 826 | 825 | 0x03,0x06,0x10 | Y
Parameter 27 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 827 | 826 | 0x03,0x06,0x10 | Y
Parameter 28 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 828 | 827 | 0x03,0x06,0x10 | Y
Parameter 29 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 829 | 828 | 0x03,0x06,0x10 | Y
Parameter 30 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 830 | 829 | 0x03,0x06,0x10 | Y
Parameter 31 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 831 | 830 | 0x03,0x06,0x10 | Y
Parameter 32 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 832 | 831 | 0x03,0x06,0x10 | Y
Parameter 33 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 833 | 832 | 0x03,0x06,0x10 | Y
Parameter 34 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 834 | 833 | 0x03,0x06,0x10 | Y
Parameter 35 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 835 | 834 | 0x03,0x06,0x10 | Y
Parameter 36 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 836 | 835 | 0x03,0x06,0x10 | Y
Parameter 37 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 837 | 836 | 0x03,0x06,0x10 | Y
Parameter 38 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 838 | 837 | 0x03,0x06,0x10 | Y
Parameter 39 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 839 | 838 | 0x03,0x06,0x10 | Y
Parameter 40 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 840 | 839 | 0x03,0x06,0x10 | Y
Parameter 41 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 841 | 840 | 0x03,0x06,0x10 | Y
Parameter 42 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 842 | 841 | 0x03,0x06,0x10 | Y
Parameter 43 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 843 | 842 | 0x03,0x06,0x10 | Y
Parameter 44 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 844 | 843 | 0x03,0x06,0x10 | Y
Parameter 45 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 845 | 844 | 0x03,0x06,0x10 | Y
Parameter 46 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 846 | 845 | 0x03,0x06,0x10 | Y
Parameter 47 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 847 | 846 | 0x03,0x06,0x10 | Y
Parameter 48 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 848 | 847 | 0x03,0x06,0x10 | Y
Parameter 49 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 849 | 848 | 0x03,0x06,0x10 | Y
Parameter 50 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 850 | 849 | 0x03,0x06,0x10 | Y
Parameter 51 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 851 | 850 | 0x03,0x06,0x10 | Y
Parameter 52 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 852 | 851 | 0x03,0x06,0x10 | Y
Parameter 53 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 853 | 852 | 0x03,0x06,0x10 | Y
Parameter 54 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 854 | 853 | 0x03,0x06,0x10 | Y
Parameter 55 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 855 | 854 | 0x03,0x06,0x10 | Y
Parameter 56 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 856 | 855 | 0x03,0x06,0x10 | Y
Parameter 57 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 857 | 856 | 0x03,0x06,0x10 | Y
Parameter 58 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 858 | 857 | 0x03,0x06,0x10 | Y
Parameter 59 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 859 | 858 | 0x03,0x06,0x10 | Y
Parameter 60 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 860 | 859 | 0x03,0x06,0x10 | Y
Parameter 61 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 861 | 860 | 0x03,0x06,0x10 | Y
Parameter 62 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 862 | 861 | 0x03,0x06,0x10 | Y
Parameter 63 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 863 | 862 | 0x03,0x06,0x10 | Y
Parameter 64 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 864 | 863 | 0x03,0x06,0x10 | Y
Parameter 65 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 865 | 864 | 0x03,0x06,0x10 | Y
Parameter 66 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 866 | 865 | 0x03,0x06,0x10 | Y
Parameter 67 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 867 | 866 | 0x03,0x06,0x10 | Y
Parameter 68 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 868 | 867 | 0x03,0x06,0x10 | Y
Parameter 69 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 869 | 868 | 0x03,0x06,0x10 | Y
Parameter 70 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 870 | 869 | 0x03,0x06,0x10 | Y
Parameter 71 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 871 | 870 | 0x03,0x06,0x10 | Y
Parameter 72 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 872 | 871 | 0x03,0x06,0x10 | Y
Parameter 73 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 873 | 872 | 0x03,0x06,0x10 | Y
Parameter 74 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 874 | 873 | 0x03,0x06,0x10 | Y
Parameter 75 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 875 | 874 | 0x03,0x06,0x10 | Y
Parameter 76 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 876 | 875 | 0x03,0x06,0x10 | Y
Parameter 77 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 877 | 876 | 0x03,0x06,0x10 | Y
Parameter 78 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 878 | 877 | 0x03,0x06,0x10 | Y
Parameter 79 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 879 | 878 | 0x03,0x06,0x10 | Y
Parameter 80 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 880 | 879 | 0x03,0x06,0x10 | Y
Parameter 81 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 881 | 880 | 0x03,0x06,0x10 | Y
Parameter 82 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 882 | 881 | 0x03,0x06,0x10 | Y
Parameter 83 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 883 | 882 | 0x03,0x06,0x10 | Y
Parameter 84 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 884 | 883 | 0x03,0x06,0x10 | Y
Parameter 85 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 885 | 884 | 0x03,0x06,0x10 | Y
Parameter 86 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 886 | 885 | 0x03,0x06,0x10 | Y
Parameter 87 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 887 | 886 | 0x03,0x06,0x10 | Y
Parameter 88 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 888 | 887 | 0x03,0x06,0x10 | Y
Parameter 89 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 889 | 888 | 0x03,0x06,0x10 | Y
Parameter 90 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 890 | 889 | 0x03,0x06,0x10 | Y
Parameter 91 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 891 | 890 | 0x03,0x06,0x10 | Y
Parameter 92 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 892 | 891 | 0x03,0x06,0x10 | Y
Parameter 93 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 893 | 892 | 0x03,0x06,0x10 | Y
Parameter 94 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 894 | 893 | 0x03,0x06,0x10 | Y
Parameter 95 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 895 | 894 | 0x03,0x06,0x10 | Y
Parameter 96 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 896 | 895 | 0x03,0x06,0x10 | Y
Parameter 97 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 897 | 896 | 0x03,0x06,0x10 | Y
Parameter 98 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 898 | 897 | 0x03,0x06,0x10 | Y
Parameter 99 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 899 | 898 | 0x03,0x06,0x10 | Y
Parameter 100 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 900 | 899 | 0x03,0x06,0x10 | Y
User Map values
Parameter 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 901 | 900 | 0x03,0x06,0x10 | N
Parameter 2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 902 | 901 | 0x03,0x06,0x10 | N
Parameter 3 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 903 | 902 | 0x03,0x06,0x10 | N
Parameter 4 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 904 | 903 | 0x03,0x06,0x10 | N
Parameter 5 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 905 | 904 | 0x03,0x06,0x10 | N
Parameter 6 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 906 | 905 | 0x03,0x06,0x10 | N
Parameter 7 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 907 | 906 | 0x03,0x06,0x10 | N
Parameter 8 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 908 | 907 | 0x03,0x06,0x10 | N
Parameter 9 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 909 | 908 | 0x03,0x06,0x10 | N
Parameter 10 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 910 | 909 | 0x03,0x06,0x10 | N
Parameter 11 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 911 | 910 | 0x03,0x06,0x10 | N
Parameter 12 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 912 | 911 | 0x03,0x06,0x10 | N
Parameter 13 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 913 | 912 | 0x03,0x06,0x10 | N
Parameter 14 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 914 | 913 | 0x03,0x06,0x10 | N
Parameter 15 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 915 | 914 | 0x03,0x06,0x10 | N
Parameter 16 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 916 | 915 | 0x03,0x06,0x10 | N
Parameter 17 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 917 | 916 | 0x03,0x06,0x10 | N
Parameter 18 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 918 | 917 | 0x03,0x06,0x10 | N
Parameter 19 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 919 | 918 | 0x03,0x06,0x10 | N
Parameter 20 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 920 | 919 | 0x03,0x06,0x10 | N
Parameter 21 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 921 | 920 | 0x03,0x06,0x10 | N
Parameter 22 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 922 | 921 | 0x03,0x06,0x10 | N
Parameter 23 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 923 | 922 | 0x03,0x06,0x10 | N
Parameter 24 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 924 | 923 | 0x03,0x06,0x10 | N
Parameter 25 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 925 | 924 | 0x03,0x06,0x10 | N
Parameter 26 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 926 | 925 | 0x03,0x06,0x10 | N
Parameter 27 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 927 | 926 | 0x03,0x06,0x10 | N
Parameter 28 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 928 | 927 | 0x03,0x06,0x10 | N
Parameter 29 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 929 | 928 | 0x03,0x06,0x10 | N
Parameter 30 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 930 | 929 | 0x03,0x06,0x10 | N
Parameter 31 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 931 | 930 | 0x03,0x06,0x10 | N
Parameter 32 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 932 | 931 | 0x03,0x06,0x10 | N
Parameter 33 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 933 | 932 | 0x03,0x06,0x10 | N
Parameter 34 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 934 | 933 | 0x03,0x06,0x10 | N
Parameter 35 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 935 | 934 | 0x03,0x06,0x10 | N
Parameter 36 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 936 | 935 | 0x03,0x06,0x10 | N
Parameter 37 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 937 | 936 | 0x03,0x06,0x10 | N
Parameter 38 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 938 | 937 | 0x03,0x06,0x10 | N
Parameter 39 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 939 | 938 | 0x03,0x06,0x10 | N
Parameter 40 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 940 | 939 | 0x03,0x06,0x10 | N
Parameter 41 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 941 | 940 | 0x03,0x06,0x10 | N
Parameter 42 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 942 | 941 | 0x03,0x06,0x10 | N
Parameter 43 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 943 | 942 | 0x03,0x06,0x10 | N
Parameter 44 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 944 | 943 | 0x03,0x06,0x10 | N
Parameter 45 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 945 | 944 | 0x03,0x06,0x10 | N
Parameter 46 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 946 | 945 | 0x03,0x06,0x10 | N
Parameter 47 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 947 | 946 | 0x03,0x06,0x10 | N
Parameter 48 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 948 | 947 | 0x03,0x06,0x10 | N
Parameter 49 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 949 | 948 | 0x03,0x06,0x10 | N
Parameter 50 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 950 | 949 | 0x03,0x06,0x10 | N
Parameter 51 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 951 | 950 | 0x03,0x06,0x10 | N
Parameter 52 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 952 | 951 | 0x03,0x06,0x10 | N
Parameter 53 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 953 | 952 | 0x03,0x06,0x10 | N
Parameter 54 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 954 | 953 | 0x03,0x06,0x10 | N
Parameter 55 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 955 | 954 | 0x03,0x06,0x10 | N
Parameter 56 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 956 | 955 | 0x03,0x06,0x10 | N
Parameter 57 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 957 | 956 | 0x03,0x06,0x10 | N
Parameter 58 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 958 | 957 | 0x03,0x06,0x10 | N
Parameter 59 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 959 | 958 | 0x03,0x06,0x10 | N
Parameter 60 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 960 | 959 | 0x03,0x06,0x10 | N
Parameter 61 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 961 | 960 | 0x03,0x06,0x10 | N
Parameter 62 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 962 | 961 | 0x03,0x06,0x10 | N
Parameter 63 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 963 | 962 | 0x03,0x06,0x10 | N
Parameter 64 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 964 | 963 | 0x03,0x06,0x10 | N
Parameter 65 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 965 | 964 | 0x03,0x06,0x10 | N
Parameter 66 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 966 | 965 | 0x03,0x06,0x10 | N
Parameter 67 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 967 | 966 | 0x03,0x06,0x10 | N
Parameter 68 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 968 | 967 | 0x03,0x06,0x10 | N
Parameter 69 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 969 | 968 | 0x03,0x06,0x10 | N
Parameter 70 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 970 | 969 | 0x03,0x06,0x10 | N
Parameter 71 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 971 | 970 | 0x03,0x06,0x10 | N
Parameter 72 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 972 | 971 | 0x03,0x06,0x10 | N
Parameter 73 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 973 | 972 | 0x03,0x06,0x10 | N
Parameter 74 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 974 | 973 | 0x03,0x06,0x10 | N
Parameter 75 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 975 | 974 | 0x03,0x06,0x10 | N
Parameter 76 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 976 | 975 | 0x03,0x06,0x10 | N
Parameter 77 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 977 | 976 | 0x03,0x06,0x10 | N
Parameter 78 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 978 | 977 | 0x03,0x06,0x10 | N
Parameter 79 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 979 | 978 | 0x03,0x06,0x10 | N
Parameter 80 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 980 | 979 | 0x03,0x06,0x10 | N
Parameter 81 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 981 | 980 | 0x03,0x06,0x10 | N
Parameter 82 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 982 | 981 | 0x03,0x06,0x10 | N
Parameter 83 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 983 | 982 | 0x03,0x06,0x10 | N
Parameter 84 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 984 | 983 | 0x03,0x06,0x10 | N
Parameter 85 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 985 | 984 | 0x03,0x06,0x10 | N
Parameter 86 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 986 | 985 | 0x03,0x06,0x10 | N
Parameter 87 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 987 | 986 | 0x03,0x06,0x10 | N
Parameter 88 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 988 | 987 | 0x03,0x06,0x10 | N
Parameter 89 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 989 | 988 | 0x03,0x06,0x10 | N
Parameter 90 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 990 | 989 | 0x03,0x06,0x10 | N
Parameter 91 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 991 | 990 | 0x03,0x06,0x10 | N
Parameter 92 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 992 | 991 | 0x03,0x06,0x10 | N
Parameter 93 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 993 | 992 | 0x03,0x06,0x10 | N
Parameter 94 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 994 | 993 | 0x03,0x06,0x10 | N
Parameter 95 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 995 | 994 | 0x03,0x06,0x10 | N
Parameter 96 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 996 | 995 | 0x03,0x06,0x10 | N
Parameter 97 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 997 | 996 | 0x03,0x06,0x10 | N
Parameter 98 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 998 | 997 | 0x03,0x06,0x10 | N
Parameter 99 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 999 | 998 | 0x03,0x06,0x10 | N
Parameter 100 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1000 | 999 | 0x03,0x06,0x10 | N
HMI registers
Reserved | UINT16 | 40 | 20 | 0 | 65535 | 1 | 1 | R | 1001 | 1000 | 0x03 | N
HMI Keys (Programmable) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1021 | 1020 | 0x03 | N
Reserved | UINT16 | 358 | 179 | 0 | 65535 | 1 | 1 | R | 1022 | 1021 | 0x03 | N
Custom Logic Variables
Custom logic status register | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1201 | 1200 | 0x03 | N
Custom logic version | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1202 | 1201 | 0x03 | N
Custom logic memory space | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1203 | 1202 | 0x03 | N
Custom logic memory used | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1204 | 1203 | 0x03 | N
Custom logic temporary space | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1205 | 1204 | 0x03 | N
Custom logic non-volatile space | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1206 | 1205 | 0x03 | N
Reserved | UINT16 | 88 | 44 | 0 | 0 | 1 | 1 | R | 1207 | 1206 | 0x03 | N
Custom logic setting register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1251 | 1250 | 0x03,0x06,0x10 | Y
Reserved | UINT16 | 38 | 19 | 0 | 0 | 1 | 1 | RW | 1252 | 1251 | 0x03,0x06,0x10 | N
Custom logic command register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1271 | 1270 | 0x03,0x06,0x10 | Y
Reserved | UINT16 | 18 | 9 | 0 | 0 | 1 | 1 | RW | 1272 | 1271 | 0x03,0x06,0x10 | N
Custom logic monitoring register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1281 | 1280 | 0x03 | N
Reserved | UINT16 | 20 | 10 | 0 | 0 | 1 | 1 | R | 1282 | 1281 | 0x03 | N
TesysTera CL DO Input Information | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 1292 | 1291 | 0x03 | N |  |  | Bit 0:CL DO1 Input information Bit 1:CL DO2 Input information Bit 2:CL DO3 Input information Bit 3:CL DO4 Input information Bit 4:CL DO5 Input information Bit 5:CL DO6 Input information Bit 6:CL DO7 Input information Bit 7:CL DO8 Input information Bit 8:CL DO9 Input information Bit 9:CL DO10 Input information Bit 10:CL DO11 Input information Bit 11:CL DO12 Input information Bit 12:CL DO13 Input information Bit 13:NA Bit 14:NA Bit 15:NA
Reserved | UINT16 | 18 | 9 | 0 | 65535 | 1 | 1 | R | 1293 | 1292 | 0x03 | N
Custom logic general purpose register1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1302 | 1301 | 0x03,0x06,0x10 | N
Custom logic general purpose register2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1303 | 1302 | 0x03,0x06,0x10 | N
Custom logic general purpose register3 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1304 | 1303 | 0x03,0x06,0x10 | N
Custom logic general purpose register4 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1305 | 1304 | 0x03,0x06,0x10 | N
Custom logic general purpose register5 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1306 | 1305 | 0x03,0x06,0x10 | N
Custom logic general purpose register6 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1307 | 1306 | 0x03,0x06,0x10 | N
Custom logic general purpose register7 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1308 | 1307 | 0x03,0x06,0x10 | N
Custom logic general purpose register8 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1309 | 1308 | 0x03,0x06,0x10 | N
Custom logic general purpose register9 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1310 | 1309 | 0x03,0x06,0x10 | N
Custom logic general purpose register10 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1311 | 1310 | 0x03,0x06,0x10 | N
Custom logic general purpose register11 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1312 | 1311 | 0x03,0x06,0x10 | N
Custom logic general purpose register12 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1313 | 1312 | 0x03,0x06,0x10 | N
Custom logic general purpose register13 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1314 | 1313 | 0x03,0x06,0x10 | N
Custom logic general purpose register14 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1315 | 1314 | 0x03,0x06,0x10 | N
Custom logic general purpose register15 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1316 | 1315 | 0x03,0x06,0x10 | N
Custom logic general purpose register16 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1317 | 1316 | 0x03,0x06,0x10 | N
Custom logic general purpose register17 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1318 | 1317 | 0x03,0x06,0x10 | N
Custom logic general purpose register18 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1319 | 1318 | 0x03,0x06,0x10 | N
Custom logic general purpose register19 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1320 | 1319 | 0x03,0x06,0x10 | N
Custom logic general purpose register20 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1321 | 1320 | 0x03,0x06,0x10 | N
Custom logic general purpose register21 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1322 | 1321 | 0x03,0x06,0x10 | N
Custom logic general purpose register22 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1323 | 1322 | 0x03,0x06,0x10 | N
Custom logic general purpose register23 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1324 | 1323 | 0x03,0x06,0x10 | N
Custom logic general purpose register24 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1325 | 1324 | 0x03,0x06,0x10 | N
Custom logic general purpose register25 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1326 | 1325 | 0x03,0x06,0x10 | N
Custom logic general purpose register26 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1327 | 1326 | 0x03,0x06,0x10 | N
Custom logic general purpose register27 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1328 | 1327 | 0x03,0x06,0x10 | N
Custom logic general purpose register28 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1329 | 1328 | 0x03,0x06,0x10 | N
Custom logic general purpose register29 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1330 | 1329 | 0x03,0x06,0x10 | N
Custom logic general purpose register30 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1331 | 1330 | 0x03,0x06,0x10 | N
Custom logic general purpose register31 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1332 | 1331 | 0x03,0x06,0x10 | N
Custom logic general purpose register32 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1333 | 1332 | 0x03,0x06,0x10 | N
Custom logic general purpose register33 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1334 | 1333 | 0x03,0x06,0x10 | N
Custom logic general purpose register34 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1335 | 1334 | 0x03,0x06,0x10 | N
Custom logic general purpose register35 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1336 | 1335 | 0x03,0x06,0x10 | N
Custom logic general purpose register36 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1337 | 1336 | 0x03,0x06,0x10 | N
Custom logic general purpose register37 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1338 | 1337 | 0x03,0x06,0x10 | N
Custom logic general purpose register38 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1339 | 1338 | 0x03,0x06,0x10 | N
Custom logic general purpose register39 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1340 | 1339 | 0x03,0x06,0x10 | N
Custom logic general purpose register40 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1341 | 1340 | 0x03,0x06,0x10 | N
Custom logic general purpose register41 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1342 | 1341 | 0x03,0x06,0x10 | N
Custom logic general purpose register42 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1343 | 1342 | 0x03,0x06,0x10 | N
Custom logic general purpose register43 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1344 | 1343 | 0x03,0x06,0x10 | N
Custom logic general purpose register44 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1345 | 1344 | 0x03,0x06,0x10 | N
Custom logic general purpose register45 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1346 | 1345 | 0x03,0x06,0x10 | N
Custom logic general purpose register46 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1347 | 1346 | 0x03,0x06,0x10 | N
Custom logic general purpose register47 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1348 | 1347 | 0x03,0x06,0x10 | N
Custom logic general purpose register48 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1349 | 1348 | 0x03,0x06,0x10 | N
Custom logic general purpose register49 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1350 | 1349 | 0x03,0x06,0x10 | N
Custom logic general purpose register50 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1351 | 1350 | 0x03,0x06,0x10 | N
Custom logic general purpose register51 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1352 | 1351 | 0x03,0x06,0x10 | N
Custom logic general purpose register52 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1353 | 1352 | 0x03,0x06,0x10 | N
Custom logic general purpose register53 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1354 | 1353 | 0x03,0x06,0x10 | N
Custom logic general purpose register54 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1355 | 1354 | 0x03,0x06,0x10 | N
Custom logic general purpose register55 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1356 | 1355 | 0x03,0x06,0x10 | N
Custom logic general purpose register56 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1357 | 1356 | 0x03,0x06,0x10 | N
Custom logic general purpose register57 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1358 | 1357 | 0x03,0x06,0x10 | N
Custom logic general purpose register58 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1359 | 1358 | 0x03,0x06,0x10 | N
Custom logic general purpose register59 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1360 | 1359 | 0x03,0x06,0x10 | N
Custom logic general purpose register60 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1361 | 1360 | 0x03,0x06,0x10 | N
Custom logic general purpose register61 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1362 | 1361 | 0x03,0x06,0x10 | N
Custom logic general purpose register62 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1363 | 1362 | 0x03,0x06,0x10 | N
Custom logic general purpose register63 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1364 | 1363 | 0x03,0x06,0x10 | N
Custom logic general purpose register64 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1365 | 1364 | 0x03,0x06,0x10 | N
Custom logic general purpose register65 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1366 | 1365 | 0x03,0x06,0x10 | N
Custom logic general purpose register66 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1367 | 1366 | 0x03,0x06,0x10 | N
Custom logic general purpose register67 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1368 | 1367 | 0x03,0x06,0x10 | N
Custom logic general purpose register68 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1369 | 1368 | 0x03,0x06,0x10 | N
Custom logic general purpose register69 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1370 | 1369 | 0x03,0x06,0x10 | N
Custom logic general purpose register70 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1371 | 1370 | 0x03,0x06,0x10 | N
Custom logic general purpose register71 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1372 | 1371 | 0x03,0x06,0x10 | N
Custom logic general purpose register72 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1373 | 1372 | 0x03,0x06,0x10 | N
Custom logic general purpose register73 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1374 | 1373 | 0x03,0x06,0x10 | N
Custom logic general purpose register74 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1375 | 1374 | 0x03,0x06,0x10 | N
Custom logic general purpose register75 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1376 | 1375 | 0x03,0x06,0x10 | N
Custom logic general purpose register76 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1377 | 1376 | 0x03,0x06,0x10 | N
Custom logic general purpose register77 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1378 | 1377 | 0x03,0x06,0x10 | N
Custom logic general purpose register78 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1379 | 1378 | 0x03,0x06,0x10 | N
Custom logic general purpose register79 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1380 | 1379 | 0x03,0x06,0x10 | N
Custom logic general purpose register80 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1381 | 1380 | 0x03,0x06,0x10 | N
Custom logic general purpose register81 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1382 | 1381 | 0x03,0x06,0x10 | N
Custom logic general purpose register82 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1383 | 1382 | 0x03,0x06,0x10 | N
Custom logic general purpose register83 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1384 | 1383 | 0x03,0x06,0x10 | N
Custom logic general purpose register84 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1385 | 1384 | 0x03,0x06,0x10 | N
Custom logic general purpose register85 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1386 | 1385 | 0x03,0x06,0x10 | N
Custom logic general purpose register86 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1387 | 1386 | 0x03,0x06,0x10 | N
Custom logic general purpose register87 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1388 | 1387 | 0x03,0x06,0x10 | N
Custom logic general purpose register88 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1389 | 1388 | 0x03,0x06,0x10 | N
Custom logic general purpose register89 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1390 | 1389 | 0x03,0x06,0x10 | N
Custom logic general purpose register90 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1391 | 1390 | 0x03,0x06,0x10 | N
Custom logic general purpose register91 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1392 | 1391 | 0x03,0x06,0x10 | N
Custom logic general purpose register92 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1393 | 1392 | 0x03,0x06,0x10 | N
Custom logic general purpose register93 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1394 | 1393 | 0x03,0x06,0x10 | N
Custom logic general purpose register94 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1395 | 1394 | 0x03,0x06,0x10 | N
Custom logic general purpose register95 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1396 | 1395 | 0x03,0x06,0x10 | N
Custom logic general purpose register96 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1397 | 1396 | 0x03,0x06,0x10 | N
Custom logic general purpose register97 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1398 | 1397 | 0x03,0x06,0x10 | N
Custom logic general purpose register98 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1399 | 1398 | 0x03,0x06,0x10 | N
Custom logic general purpose register99 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 1400 | 1399 | 0x03,0x06,0x10 | N
Only applicable for Modbus/TCP and EIP
Mirroring Variables
[15 empty] | 140->01-> | 8C->01->
Mirror register 1: Not applicable | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2501 | 2500 | 0x03 | N |  |  | 1 | 1
Mirror register 2: Not applicable | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2502 | 2501 | 0x03 | N |  |  | 2 | 2
System Status register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2503 | 2502 | 0x03 | N |  |  | 3 | 3
System Status register 2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2504 | 2503 | 0x03 | N |  |  | 4 | 4
Logic Input status register | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2505 | 2504 | 0x03 | N |  |  | 5 | 5
Logic Output status register | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 2506 | 2505 | 0x03 | N |  |  | 6 | 6
Permissive Commands | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R/W | 2507 | 2506 | 0x03,0x06,0x10 | N |  |  | 7 | 7 | Bit 0: Permissive Command 1 Bit 1: Permissive Command 2 Bit 2: Permissive Command 3 Bit 3: Permissive Command 4 Bit 4: Permissive Command 5 Bit 5: Permissive Command 6 Bit 6: Permissive Command 7 Bit 7: Permissive Command 8
Command Register 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R/W | 2508 | 2507 | 0x03,0x06,0x10 | N |  |  | 8 | 8 | bit 0: Motor run forward / High speed forward command bit 1: Motor run reverse / High speed reverse command bit 2:Local/Remote Mode Sel 1 bit 3: Trip reset command bit 4: Local/Remote Mode Sel 2 bit 5: Self test (without trip) command bit 6: Motor low speed forward command bit 7: Motor low speed reverse command bit 8: Reset Inhibit command bit 9: Reset no of starts command bit 10: Reset no of stops command bit 11: Clear Energy command bit 12: Motor Stop command bit 13: Logic test command bit 14: Reset run hour command bit 15: Self test (with trip) command
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R/W | 2509 | 2508 | 0x03,0x06,0x10 | N |  |  | 9 | 9

## EIP Cyclic Parameter
TeSys Tera Class 1
|  |  | Assembly | 117 | T->O | Point to Point | Fixed Size | Scheduled
|  |  | Data Size | 40
|  |  | Details | Index | Parameter | Size in bytes | Remark
|  |  |  | Byte 0 | R phase current | 4
|  |  |  | Byte 4 | Y phase current | 4
|  |  |  | Byte 8 | B phase current | 4
|  |  |  | Byte 12 | motor Status | 2 | Start, Stop, Run, Inhibit, Remote Mode 3
|  |  |  | Byte 14 | Motor OP status | 2 | Pickup, alarm, Trip
|  |  |  | Byte 16 | DI status | 4
|  |  |  | Byte 20 | DO status | 4
|  |  |  | Byte 24 | Stop cause | 2
|  |  |  | Byte 26 | Thermal memory | 2
|  |  |  | Byte 28 | R phase Voltage | 4
|  |  |  | Byte 32 | Y phase Voltage | 4
|  |  |  | Byte 36 | B phase Voltage | 4
|  |  | Assembly | 107 | O->T | Point to Point | Fixed Size | Scheduled | Cyclic | Timout multiplier 16 |  |  | Run/Idle checked
|  |  | Data Size | 4
|  |  | Details | Index | Parameter | Size in bytes | Remark
|  |  |  | 0 | Command 1 | 1 | Modbus Register 704_LSB |  | bit 0: Motor run forward / High speed forward command bit 1: Motor run reverse / High speed reverse command bit 2:Local/Remote Mode Sel 1 bit 3: Trip reset command bit 4: Local/Remote Mode Sel 2 bit 5: Self test (without trip) command bit 6: Motor low speed forward command bit 7: Motor low speed reverse command
|  |  |  | 1 | Command 2 | 1 | Modbus Register 704_MSB |  | bit 0: Reset Inhibit command bit 1: Reset no of starts command bit 2: Reset no of stops command bit 3: Clear Energy command bit 4: Motor Stop command bit 5: Logic test command bit 6: Reset run hour command bit 7: Self test (with trip) command
|  |  |  | 2 | Command 3 | 1 | Modbus Register 705_LSB |  | bit 0: Clear all command Clear all parameters, except: -Motor LO1 closings count -Motor LO2 closings count -Controller internal temperature max -Thermal capacity level bit 1: NA bit 2: Clear thermal capacity level command bit 3: NA bit 4: NA bit 5: Clear Trip counter command bit 6-7: NA | Bold are not required: Bit 0,1,2 & 5 are supported
|  |  |  | 3 | Permissive Commands | 1 | Modbus Register 700 |  | Bit 0: Permissive Command 1 Bit 1: Permissive Command 2 Bit 2: Permissive Command 3 Bit 3: Permissive Command 4 Bit 4: Permissive Command 5 Bit 5: Permissive Command 6 Bit 6: Permissive Command 7 Bit 7: Permissive Command 8
|  |  | EDS Profiles | [10 empty] | The producer must have an active Exclusive Owner or Input Only connection.
star delta | heater | RDOL | Sr no | Name | O->T instance | O->T size | T->O instance | T->O size | Config Instance | Config Size | O->T IO | O->T IO | O->T LO | O->T LO
done | done | done | 1 | 0: Tera Profile | 107 | 4 | 117 | 40 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
done | done | done | 2 | 1: Tera Basic Overload | 2 | 1 | 50 | 1 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
done | done | done | 3 | 2: Tera Extended Overload | 2 | 1 | 51 | 1 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
done | done |  | 4 | 3: Tera Basic Motor Starter | 3 | 1 | 52 | 1 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
| done |  | 5 | 4: Tera Extended Contactor | 4 | 1 | 53 | 1 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
| done |  | 6 | 5: Tera Extended Motor Starter 1 | 4 | 1 | 54 | 1 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
| done |  | 7 | 6: Tera Extended Motor Starter 2 | 5 | 1 | 54 | 1 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
|  |  | 8 | 7: Tera Control and Monitoring | 100 | 6 | 110 | 8 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
| done |  | 9 | 8: Tera PKW | 101 | 8 | 111 | 8 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
|  |  | 10 | 9: Tera PKW and Extended Motor Starter | 102 | 10 | 112 | 10 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
|  |  | 11 | 10: Tera PKW and Management | 103 | 14 | 113 | 16 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
|  |  | 12 | 11: Tera E_TeSys Tera Fast Access | 105 | 6 | 115 | 12 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
|  |  | 13 | 12: Tera EIOS_TeSys Tera | 106 | 10 | 116 | 128 | 120 | 1 | 199 | 0 | 198 | 0 | Remove Run/idle header check
|  |  |  | Reference | Tesy T Ethernet Communication guide |  |  | DOCA0129EN-03 07/2023
Output Assembly Data
|  |  | Instance 2: Basic Overload |  | Ethernet Communication Guide
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | TripReset | Reserved | Reserved
Instance 3: Basic Motor Starter
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | TripReset | Reserved | Run 1
Instance 4: Extended Contactor
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Run 2 | Run 1
Instance 5: Extended Motor Starter
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | TripReset | Run 2 | Run 1
NOTE: TripReset, Run1, and Run2 are commands in the Control register 1.
Instance 100: LTMR Control Registers
This assembly contains several control registers commonly used with an LTMR device.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5
|  |  | path: 6C : 01 : 05 |  | path: 6C : 01 : 04 |  | path: 6C : 01 : 01
|  |  | (Register 704) |  | (Register 703) |  | (Register 700)
|  |  | LSB (least significant byte) | MSB (most significant byte) | LSB Reserved (value = 0) | MSB Reserved (value = 0) | LSB | MSB
|  |  | Instance 101: PKW Request Object | [5 empty] | https://www.se.com/in/en/download/document/DOCA0129EN/
This assembly is vendor-specific. It is used to implement the request object of PKW protocol.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7
Instance 102: PKW Request and Extended Motor Starter This assembly is vendor-specific.
|  |  | Bytes 0 to 7 | Byte 8 | Byte 9
|  |  | See Instance 101 above. | Reserved (value=0) | See Instance 5 above.
Instance 103: PKW Request and LTMR Control Registers This assembly is vendor-specific.
|  |  | Bytes 0 to 7 | Byte 8 to 13
|  |  | See Instance 101 above. | See Instance 100 above.
Instance 105: E_TeSys T FastAccess Output
This assembly is vendor-specific. All registers are in little endian.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5
|  |  | path: 8C : 01 : 07 |  | path: 8C : 01 : 08 |  | path: 8C : 01 : 09
|  |  | (Register 2506) |  | (Register 2507) |  | (Register 2508)
Instance 106: EIOS_TeSys T Output
This assembly is vendor-specific. All registers are in little endian.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5
|  |  | path: 6C : 01 : 01 |  | path: 6C : 01 : 02 |  | path: 6C : 01 : 03
|  |  | (Register 700) |  | Reserved (value = 0) |  | Reserved (value = 0)
|  |  | Byte 6 | Byte 7 | Byte 8 | Byte 9
|  |  | path: 6C : 01 : 04 |  | path: 6C : 01 : 05
|  |  | Reserved (value = 0) |  | (Register 704)
RUN1 = is mapped to 704 register bit 0
RUN2 = is mapped to 704 register bit 1
Input Assembly Data
Instance 50: Basic Overload
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Tripped
Instance 51: Extended Overload
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Alarm | Tripped
Instance 52: Basic Motor Starter
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | Reserved | Reserved | Reserved | Running1 | Reserved | Tripped
Instance 53: Extended Motor Starter 1
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | CntrlfromNet | Ready | Reserved | Running1 | Alarm | Tripped
Instance 54: Extended Motor Starter 2
|  |  | Byte | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0
|  |  | 0 | Reserved | Reserved | CntrlfromNet | Ready | Running2 | Running1 | Alarm | Tripped
NOTE: The instances contain data processed from the System status register 1 and the Control register 1:
• CntrlfromNet = In remote (status bit)
• Ready = System ready (status bit)
• Running2 = Motor running (status bit) AND Motor run reverse command (control bit)
• Running1 = Motor running (status bit) AND Motor run forward command (control bit)
• Alarm = System alarm (status bit)
• Trip = System Trip (status bit) OR System Tripped (status bit)
Instance 110: LTMR Monitoring Registers (with dynamic configuration)
This assembly contains several monitoring registers commonly used with an LTMR device. You can choose registers by setting attributes 1...4 of TeSys T Monitoring Control Object. See TeSys T Monitoring and Control Object, page 84 for more information.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7
|  |  | Value of register pointed to in path: C6 : 01 : 01 |  | Value of register pointed to in path: C6: 01 : 02 |  | Value of register pointed to in path: C6 : 01 : 03 |  | Value of register pointed to in path: C6 : 01 : 04
|  |  | Register 455 at power-up |  | Register 456 at power-up |  | Register 457 at power-up |  | Register 459 at power-up
|  |  | LSB | MSB | LSB | MSB | LSB | MSB | LSB | MSB
Instance 111: PKW Response Object
This assembly is vendor-specific. It is used to implement the response object of PKW protocol.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7
See PKW, page 81 for details.
Instance 112: PKW Response and Extended Motor Starter This assembly is vendor-specific.
|  |  | Bytes 0 to 7 | Byte 8 | Byte 9
|  |  | See Instance 111 above. | Reserved (value=0) | See Instance 54 above.
Instance 113: PKW Response and LTMR Monitoring Registers This assembly is vendor-specific.
|  |  | Bytes 0 to 7 | Byte 8 to 15
|  |  | See Instance 111 above. | See Instance 110 above.
Instance 115: E_TeSys T FastAccess Input
This assembly is vendor-specific. All registers are in little endian.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5
|  |  | path: 8C : 01 : 01 |  | path: 8C : 01 : 02 |  | path: 8C : 01 : 03
|  |  | (Register 2500) |  | (Register 2501) |  | (Register 2502)
|  |  | Byte 6 | Byte 7 | Byte 8 | Byte 9 | Byte 10 | Byte 11
|  |  | path: 8C : 01 : 04 |  | path: 8C : 01 : 05 |  | path: 8C : 01 : 06
|  |  | (Register 2503) |  | (Register 2504) |  | (Register 2505)
Instance 116: EIOS_TeSys T Input
This assembly is vendor specific. All registers are in little endian.
|  |  | Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7
|  |  | path: 68 : 01 : 02 |  | path: 68 : 01 : 03 |  | path: 68 : 01 : 04 |  | path: 68 : 01 : 05
|  |  | (Register 451) |  | (Register 452) |  | (Register 453) |  | (Register 454)
|  |  | Byte 8 | Byte 9 | Byte 10 | Byte 11 | Byte 12 | Byte 13 | Byte 14 | Byte 15
|  |  | path: 68 : 01 : 06 |  | path: 68 : 01 : 07 |  | path: 68 : 01 : 08 |  | path: 68 : 01 : 09
|  |  | (Register 455) |  | (Register 456) |  | (Register 457) |  | (Register 458)
|  |  | Byte 16 | Byte 17 | Byte 18 | Byte 19 | Byte 20 | Byte 21 | Byte 22 | Byte 23
|  |  | path: 68 : 01 : 0A |  | path: 68 : 01 : 0B |  | path: 68 : 01 : 0C |  | path: 68 : 01 : 0D
|  |  | (Register 459) |  | (Register 460) |  | (Register 461) |  | (Register 462)
|  |  | Byte 24 | Byte 25 | Byte 26 | Byte 27 | Byte 28 | Byte 29 | Byte 30 | Byte 31
|  |  | path: 68 : 01 : 0E |  | path: 68 : 01 : 0F |  | path: 68 : 01 : 10 |  | path: 68 : 01 : 11
|  |  | (Register 463) |  | (Register 464) |  | (Register 465) |  | (Register 466)
|  |  | Byte 32 | Byte 33 | Byte 34 | Byte 35 | Byte 36 | Byte 37 | Byte 38 | Byte 39
|  |  | path: 68 : 01 : 12 |  | path: 68 : 01 : 13 |  | path: 68 : 01 : 14 |  | path: 68 : 01 : 15
|  |  | (Register 467) |  | (Register 468) |  | (Register 469) |  | (Register 470)
|  |  | Byte 40 | Byte 41 | Byte 42 | Byte 43 | Byte 44 | Byte 45 | Byte 46 | Byte 47
|  |  | path: 68 : 01 : 16 |  | path: 68 : 01 : 17 |  | path: 68 : 01 : 18 |  | path: 68 : 01 : 19
|  |  | (Register 471) |  | (Register 472) |  | (Register 473) |  | (Register 474)
|  |  | Byte 48 | Byte 49 | Byte 50 | Byte 51 | Byte 52 | Byte 53 | Byte 54 | Byte 55
|  |  | path: 68 : 01 : 1A |  | path: 68 : 01 : 1B |  | path: 68 : 01 : 1C |  | path: 68 : 01 : 1D
|  |  | (Register 475) |  | (Register 476) |  | (Register 477) |  | (Register 478)
|  |  | Byte 56 | Byte 57 | Byte 58 | Byte 59 | Byte 60 | Byte 61 | Byte 62 | Byte 63
|  |  | path: 68 : 01 : 1E |  | path: 68 : 01 : 1F |  | path: 68 : 01 : 20 |  | path: 68 : 01 : 21
|  |  | (Register 479) |  | (Register 480) |  | (Register 481) |  | (Register 482)
|  |  | Byte 64 | Byte 65 | Byte 66 | Byte 67 | Byte 68 | Byte 69 | Byte 70 | Byte 71
|  |  | path: 68 : 01 : 22 |  | path: 68 : 01 : 23 |  | path: 68 : 01 : 24 |  | path: 68 : 01 : 25
|  |  | (Register 483) |  | (Register 484) |  | (Register 485) |  | (Register 486)
|  |  | Byte 72 | Byte 73 | Byte 74 | Byte 75 | Byte 76 | Byte 77 | Byte 78 | Byte 79
|  |  | path: 68 : 01 : 26 |  | path: 68 : 01 : 27 |  | path: 68 : 01 : 28 |  | path: 68 : 01 : 29
|  |  | (Register 487) |  | (Register 488) |  | (Register 489) |  | (Register 490)
|  |  | Byte 80 | Byte 81 | Byte 82 | Byte 83 | Byte 84 | Byte 85 | Byte 86 | Byte 87
|  |  | path: 68 : 01 : 2A |  | path: 68 : 01 : 2B |  | path: 68 : 01 : 2C |  | path: 68 : 01 : 2D
|  |  | (Register 491) |  | (Register 492) |  | (Register 493) |  | (Register 494)
|  |  | Byte 88 | Byte 89 | Byte 90 | Byte 91 | Byte 92 | Byte 93 | Byte 94 | Byte 95
|  |  | path: 68 : 01 : 2E |  | path: 68 : 01 : 2F |  | path: 68 : 01 : 30 |  | path: 68 : 01 : 31
|  |  | (Register 495) |  | (Register 496) |  | (Register 497) |  | (Register 498)
|  |  | Byte 96 | Byte 97 | Byte 98 | Byte 99 | Byte 100 | Byte 101 | Byte 102 | Byte 103
|  |  | path: 68 : 01 : 32 |  | path: 68 : 01 : 33 |  | path: 68 : 01 : 34 |  | path: 68 : 01 : 35
|  |  | (Register 499) |  | (Register 500) |  | (Register 501) |  | (Register 502)
|  |  | Byte 104 | Byte 105 | Byte 106 | Byte 107 | Byte 108 | Byte 109 | Byte 110 | Byte 111
|  |  | path: 68 : 01 : 36 |  | path: 68 : 01 : 37 |  | path: 68 : 01 : 38 |  | path: 68 : 01 : 39
|  |  | (Register 503) |  | (Register 504) |  | (Register 505) |  | (Register 506)
|  |  | Byte 112 | Byte 113 | Byte 114 | Byte 115 | Byte 116 | Byte 117 | Byte 118 | Byte 119
|  |  | path: 68 : 01 : 3A |  | path: 68 : 01 : 3B |  | path: 68 : 01 : 3C |  | path: 68 : 01 : 3D
|  |  | (Register 507) |  | (Register 508) |  | (Register 509) |  | (Register 510)
|  |  | Byte 120 | Byte 121 | Byte 122 | Byte 123 | Byte 124 | Byte 125 | Byte 126 | Byte 127
|  |  | path: 68 : 01 : 3E |  | path: 68 : 01 : 3F |  | path: 68 : 01 : 40 |  | path: 68 : 01 : 41
|  |  | (Register 511) |  | (Register 512) |  | (Register 513) |  | (Register 514)
Note on K25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reference: bit 0: Clear all command Clear all parameters, except: -Motor LO1 closings count -Motor LO2 closings count -Controller internal temperature max -Thermal capacity level bit 1: Reserved bit 2: Clear thermal capacity level command bit 3: Clear controller settings command bit 4: Clear network port settings command bit 5: Clear Trip counter command bit 6: Factory reset command bit 7: Soft starter reset command bits 8-12: Reserved bit 13: Store reference start curve command bit 14: Clear trip records command bit 15: Clear event records command

## Protection Settings
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Current protection
Thermal overload |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43501 | 3501 | 3500 | 0x03,0x06,0x10 | Y | 3 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Service Factor | UINT16 | 2 | 1 | 100 | 150 | 5 | 1/100 | RW | 43502 | 3502 | 3501 | 0x03,0x06,0x10 | Y | 115
Trip Class | UINT16 | 2 | 1 | 5 | 40 | 5 | 1 | RW | 43503 | 3503 | 3502 | 0x03,0x06,0x10 | Y | 10
Alarm level | UINT16 | 2 | 1 | 80 | 100 | 5 | 1 | RW | 43504 | 3504 | 3503 | 0x03,0x06,0x10 | Y | 80 | %TM
Reset Mode | BITMAP | 2 | 1 | 1 | 8 | 1 | 1 | RW | 43505 | 3505 | 3504 | 0x03,0x06,0x10 | Y | 8 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Thermal Reset level | UINT16 | 2 | 1 | 30 | 95 | 5 | 1 | RW | 43506 | 3506 | 3505 | 0x03,0x06,0x10 | Y | 90 | %TM
Start Inhibit level | UINT16 | 2 | 1 | 5 | 100 | 5 | 1 | RW | 43507 | 3507 | 3506 | 0x03,0x06,0x10 | Y | 90 | %TM
Cool Down Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43508 | 3508 | 3507 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Cool Down Time | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43509 | 3509 | 3508 | 0x03,0x06,0x10 | Y | 0 | Seconds
Pause Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43510 | 3510 | 3509 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Pause Time | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43511 | 3511 | 3510 | 0x03,0x06,0x10 | Y | 0 | Seconds
Block Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43512 | 3512 | 3511 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Block Level | UINT16 | 2 | 1 | 80 | 95 | 5 | 1 | RW | 43513 | 3513 | 3512 | 0x03,0x06,0x10 | Y | 80 | %TM
Block time | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43514 | 3514 | 3513 | 0x03,0x06,0x10 | Y | 0 | Seconds
Auxillary Fan | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43515 | 3515 | 3514 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43516 | 3516 | 3515 | 0x03,0x06,0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43517 | 3517 | 3516 | 0x03,0x06,0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43518 | 3518 | 3517 | 0x03,0x06,0x10 | Y | 0
Stalled Rotor |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43519 | 3519 | 3518 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 50 | 1000 | 1 | 1 | RW | 43520 | 3520 | 3519 | 0x03,0x06,0x10 | Y | 200 | %IFLC
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43521 | 3521 | 3520 | 0x03,0x06,0x10 | Y | 20 | Seconds
Alarm level | UINT16 | 2 | 1 | 50 | 1000 | 1 | 1 | RW | 43522 | 3522 | 3521 | 0x03,0x06,0x10 | Y | 200 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43523 | 3523 | 3522 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43524 | 3524 | 3523 | 0x03,0x06,0x10 | Y | 0 | Seconds
Locked Rotor
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43525 | 3525 | 3524 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 150 | 1000 | 1 | 1 | RW | 43526 | 3526 | 3525 | 0x03,0x06,0x10 | Y | 200 | %IFLC
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43527 | 3527 | 3526 | 0x03,0x06,0x10 | Y | 100 | Seconds
Alarm level | UINT16 | 2 | 1 | 150 | 1000 | 1 | 1 | RW | 43528 | 3528 | 3527 | 0x03,0x06,0x10 | Y | 200 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43529 | 3529 | 3528 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43530 | 3530 | 3529 | 0x03,0x06,0x10 | Y | 0 | Seconds
Definite time Overcurrent
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43531 | 3531 | 3530 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43532 | 3532 | 3531 | 0x03,0x06,0x10 | Y | 110 | %IFLC
Time delay during Motor Start (TpS) | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43533 | 3533 | 3532 | 0x03,0x06,0x10 | Y | 300 | Seconds
Time delay during Motor Run (TpR) | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43534 | 3534 | 3533 | 0x03,0x06,0x10 | Y | 200 | Seconds
Alarm level | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43535 | 3535 | 3534 | 0x03,0x06,0x10 | Y | 110 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43536 | 3536 | 3535 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43537 | 3537 | 3536 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43538 | 3538 | 3537 | 0x03,0x06,0x10 | N | 0
Normal inverse overcurrent
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43539 | 3539 | 3538 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43540 | 3540 | 3539 | 0x03,0x06,0x10 | Y | 50 | %IFLC
Time Multiplier (TMS) | UINT16 | 2 | 1 | 1 | 200 | 1 | 1/10 | RW | 43541 | 3541 | 3540 | 0x03,0x06,0x10 | Y | 1
Alarm level | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43542 | 3542 | 3541 | 0x03,0x06,0x10 | Y | 50 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43543 | 3543 | 3542 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43544 | 3544 | 3543 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43545 | 3545 | 3544 | 0x03,0x06,0x10 | N | 0
Short time overcurrent
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43546 | 3546 | 3545 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 100 | 1000 | 1 | 1 | RW | 43547 | 3547 | 3546 | 0x03,0x06,0x10 | Y | 100 | %IFLC
Time delay | UINT16 | 2 | 1 | 5 | 1000 | 1 | 1/100 | RW | 43548 | 3548 | 3547 | 0x03,0x06,0x10 | Y | 5 | Seconds
Alarm level | UINT16 | 2 | 1 | 100 | 1000 | 1 | 1 | RW | 43549 | 3549 | 3548 | 0x03,0x06,0x10 | Y | 100 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43550 | 3550 | 3549 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43551 | 3551 | 3550 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43552 | 3552 | 3551 | 0x03,0x06,0x10 | N | 0
Calculated ground fault
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43553 | 3553 | 3552 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 10 | 500 | 1 | 1 | RW | 43554 | 3554 | 3553 | 0x03,0x06,0x10 | Y | 20 | %IFLC
Time delay | UINT16 | 2 | 1 | 5 | 60000 | 1 | 1/100 | RW | 43555 | 3555 | 3554 | 0x03,0x06,0x10 | Y | 20 | Seconds
Alarm level | UINT16 | 2 | 1 | 10 | 500 | 1 | 1 | RW | 43556 | 3556 | 3555 | 0x03,0x06,0x10 | Y | 20 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43557 | 3557 | 3556 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43558 | 3558 | 3557 | 0x03,0x06,0x10 | Y | 0 | Seconds
Function while motor starting | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43559 | 3559 | 3558 | 0x03,0x06,0x10 | N | 0 |  | 0 - Disable 1 - Enable
Measured ground fault
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43560 | 3560 | 3559 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 20 | 20000 | 10 | 1 | RW | 43561 | 3561 | 3560 | 0x03,0x06,0x10 | Y | 30 | mA
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43562 | 3562 | 3561 | 0x03,0x06,0x10 | Y | 1 | Seconds
Alarm level | UINT16 | 2 | 1 | 20 | 20000 | 10 | 1 | RW | 43563 | 3563 | 3562 | 0x03,0x06,0x10 | Y | 30 | mA
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43564 | 3564 | 3563 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43565 | 3565 | 3564 | 0x03,0x06,0x10 | Y | 0 | Seconds
Function while motor starting | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43566 | 3566 | 3565 | 0x03,0x06,0x10 | N | 0 |  | 0 - Disable 1 - Enable
Phase Under current
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43567 | 3567 | 3566 | 0x03,0x06,0x10 | Y | 1 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 15 | 100 | 1 | 1 | RW | 43568 | 3568 | 3567 | 0x03,0x06,0x10 | Y | 50 | %IFLC
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43569 | 3569 | 3568 | 0x03,0x06,0x10 | Y | 100 | Seconds
Alarm level | UINT16 | 2 | 1 | 15 | 100 | 1 | 1 | RW | 43570 | 3570 | 3569 | 0x03,0x06,0x10 | Y | 50 | %IFLC
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43571 | 3571 | 3570 | 0x03,0x06,0x10 | Y | 8 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43572 | 3572 | 3571 | 0x03,0x06,0x10 | Y | 50 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43573 | 3573 | 3572 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43574 | 3574 | 3573 | 0x03,0x06,0x10 | N | 0
Current Imbalace
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43575 | 3575 | 3574 | 0x03,0x06,0x10 | Y | 3 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 5 | 100 | 5 | 1 | RW | 43576 | 3576 | 3575 | 0x03,0x06,0x10 | Y | 20 | %
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43577 | 3577 | 3576 | 0x03,0x06,0x10 | Y | 50 | Seconds
Alarm level | UINT16 | 2 | 1 | 5 | 100 | 5 | 1 | RW | 43578 | 3578 | 3577 | 0x03,0x06,0x10 | Y | 20 | %
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43579 | 3579 | 3578 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43580 | 3580 | 3579 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43581 | 3581 | 3580 | 0x03,0x06,0x10 | N | 0
Phase Loss Settings:IPL |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43582 | 3582 | 3581 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43583 | 3583 | 3582 | 0x03,0x06,0x10 | Y | 1 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43584 | 3584 | 3583 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43585 | 3585 | 3584 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43586 | 3586 | 3585 | 0x03,0x06,0x10 | N | 0
Phase Reversal |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43587 | 3587 | 3586 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43588 | 3588 | 3587 | 0x03,0x06,0x10 | Y | 1 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43589 | 3589 | 3588 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43590 | 3590 | 3589 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43591 | 3591 | 3590 | 0x03,0x06,0x10 | N | 0
Voltage Based Protection
Phase Under VoltagePHUV:NULL
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43626 | 3626 | 3625 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 20 | 100 | 1 | 1 | RW | 43627 | 3627 | 3626 | 0x03,0x06,0x10 | Y | 80 | %Vn
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43628 | 3628 | 3627 | 0x03,0x06,0x10 | Y | 100 | Seconds
Alarm level | UINT16 | 2 | 1 | 20 | 100 | 1 | 1 | RW | 43629 | 3629 | 3628 | 0x03,0x06,0x10 | Y | 80 | %Vn
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43630 | 3630 | 3629 | 0x03,0x06,0x10 | Y | 8 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43631 | 3631 | 3630 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43632 | 3632 | 3631 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43633 | 3633 | 3632 | 0x03,0x06,0x10 | N | 0
Phase Over Voltage
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43634 | 3634 | 3633 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 101 | 130 | 1 | 1 | RW | 43635 | 3635 | 3634 | 0x03,0x06,0x10 | Y | 110 | %Vn
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43636 | 3636 | 3635 | 0x03,0x06,0x10 | Y | 50 | Seconds
Alarm level | UINT16 | 2 | 1 | 101 | 130 | 1 | 1 | RW | 43637 | 3637 | 3636 | 0x03,0x06,0x10 | Y | 110 | %Vn
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43638 | 3638 | 3637 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43639 | 3639 | 3638 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43640 | 3640 | 3639 | 0x03,0x06,0x10 | N | 0
Phase Loss Settings |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43641 | 3641 | 3640 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43642 | 3642 | 3641 | 0x03,0x06,0x10 | Y | 1 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43643 | 3643 | 3642 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43644 | 3644 | 3643 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43645 | 3645 | 3644 | 0x03,0x06,0x10 | N | 0
Voltage Imbalace
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43646 | 3646 | 3645 | 0x03,0x06,0x10 | Y | 3 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 5 | 50 | 5 | 1 | RW | 43647 | 3647 | 3646 | 0x03,0x06,0x10 | Y | 10 | %
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43648 | 3648 | 3647 | 0x03,0x06,0x10 | Y | 100 | Seconds
Alarm level | UINT16 | 2 | 1 | 5 | 50 | 5 | 1 | RW | 43649 | 3649 | 3648 | 0x03,0x06,0x10 | N | 10 | %
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43650 | 3650 | 3649 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43651 | 3651 | 3650 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43652 | 3652 | 3651 | 0x03,0x06,0x10 | N | 0
Phase Reversal |  |  | 0 | 0 | 0 | 0 | 1 | RW | 43776 |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43653 | 3653 | 3652 | 0x03,0x06,0x10 | Y | 2 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43654 | 3654 | 3653 | 0x03,0x06,0x10 | Y | 1 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43655 | 3655 | 3654 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43656 | 3656 | 3655 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43657 | 3657 | 3656 | 0x03,0x06,0x10 | N | 0
Under Frequency |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43658 | 3658 | 3657 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 90 | 100 | 1 | 1 | RW | 43659 | 3659 | 3658 | 0x03,0x06,0x10 | Y | 94 | %Frequency
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43660 | 3660 | 3659 | 0x03,0x06,0x10 | Y | 1 | Seconds
Alarm level | UINT16 | 2 | 1 | 90 | 100 | 1 | 1 | RW | 43661 | 3661 | 3660 | 0x03,0x06,0x10 | Y | 94 | %Frequency
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43662 | 3662 | 3661 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43663 | 3663 | 3662 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43664 | 3664 | 3663 | 0x03,0x06,0x10 | N | 0
Over Frequency |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43665 | 3665 | 3664 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 100 | 110 | 1 | 1 | RW | 43666 | 3666 | 3665 | 0x03,0x06,0x10 | Y | 105 | %Frequency
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43667 | 3667 | 3666 | 0x03,0x06,0x10 | Y | 1 | Seconds
Alarm level | UINT16 | 2 | 1 | 100 | 110 | 1 | 1 | RW | 43668 | 3668 | 3667 | 0x03,0x06,0x10 | Y | 105 | %Frequency
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43669 | 3669 | 3668 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43670 | 3670 | 3669 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43671 | 3671 | 3670 | 0x03,0x06,0x10 | N | 0
Under Power |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43672 | 3672 | 3671 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43673 | 3673 | 3672 | 0x03,0x06,0x10 | Y | 60 | %Pnominal
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43674 | 3674 | 3673 | 0x03,0x06,0x10 | Y | 1 | Seconds
Alarm level | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43675 | 3675 | 3674 | 0x03,0x06,0x10 | Y | 60 | %Pnominal
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43676 | 3676 | 3675 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43677 | 3677 | 3676 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43678 | 3678 | 3677 | 0x03,0x06,0x10 | N | 0
Over Power |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43679 | 3679 | 3678 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43680 | 3680 | 3679 | 0x03,0x06,0x10 | Y | 110 | %Pnominal
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43681 | 3681 | 3680 | 0x03,0x06,0x10 | Y | 1 | Seconds
Alarm level | UINT16 | 2 | 1 | 20 | 1000 | 1 | 1 | RW | 43682 | 3682 | 3681 | 0x03,0x06,0x10 | Y | 110 | %Pnominal
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43683 | 3683 | 3682 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43684 | 3684 | 3683 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43685 | 3685 | 3684 | 0x03,0x06,0x10 | N | 0
Under Power Factor |  |  | 0 | 0 | 0 | 0 | 1 | RW | #REF! |  |  | 0x03
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43686 | 3686 | 3685 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Pickup | UINT16 | 2 | 1 | 40 | 100 | 1 | 1/100 | RW | 43687 | 3687 | 3686 | 0x03,0x06,0x10 | Y | 60 | PF
Time delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43688 | 3688 | 3687 | 0x03,0x06,0x10 | Y | 1 | Seconds
Alarm level | UINT16 | 2 | 1 | 40 | 100 | 1 | 1/100 | RW | 43689 | 3689 | 3688 | 0x03,0x06,0x10 | Y | 60 | PF
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43690 | 3690 | 3689 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43691 | 3691 | 3690 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43692 | 3692 | 3691 | 0x03,0x06,0x10 | N | 0
Control Functions
Excessive Start Time
Function | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 43751 | 3751 | 3750 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable
Time delay | UINT16 | 2 | 1 | 100 | 100 | 1 | 1/10 | RW | 43752 | 3752 | 3751 | 0x03,0x06,0x10 | Y | 100 | Seconds
Reset Mode | BITMAP | 2 | 1 | 3 | 3 | 1 | 1 | RW | 43753 | 3753 | 3752 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 0 | 1 | 1/10 | RW | 43754 | 3754 | 3753 | 0x03,0x06,0x10 | Y | 0 | Seconds
Run Threshold | UINT16 | 2 | 1 | 100 | 100 | 1 | 1 | RW | 43755 | 3755 | 3754 | 0x03,0x06,0x10 | Y | 100 | %IFLC
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43756 | 3756 | 3755 | 0x03,0x06,0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43757 | 3757 | 3756 | 0x03,0x06,0x10 | Y | 0
Voltage Dip: VDIP: NULL
Function | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 43758 | 3758 | 3757 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Load shedding 2 - Auto restart
Voltage Dip | UINT16 | 2 | 1 | 20 | 90 | 5 | 1 | RW | 43759 | 3759 | 3758 | 0x03,0x06,0x10 | Y | 90 | %Vn
Voltage Restoration | UINT16 | 2 | 1 | 20 | 95 | 5 | 1 | RW | 43760 | 3760 | 3759 | 0x03,0x06,0x10 | Y | 95 | %Vn
Voltage dip restart timeout | UINT16 | 2 | 1 | 0 | 9999 | 1 | 1 | RW | 43761 | 3761 | 3760 | 0x03,0x06,0x10 | Y | 2 | sec
Delayed restart timeout | UINT16 | 2 | 1 | 0 | 301 | 1 | 1 | RW | 43762 | 3762 | 3761 | 0x03,0x06,0x10 | Y | 4 | sec
Bypass STOP_DI | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43763 | 3763 | 3762 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
immediate restart timeout | UINT16 | 2 | 1 | 0 | 4 | 1 | 1/10 | RW | 43764 | 3764 | 3763 | 0x03,0x06,0x10 | Y | 2
Load shedding timeout | UINT16 | 2 | 1 | 1 | 9999 | 1 | 1 | RW | 43765 | 3765 | 3764 | 0x03,0x06,0x10 | Y | 10
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43766 | 3766 | 3765 | 0x03,0x06,0x10 | Y | 0
Maximum number of Starts
Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43767 | 3767 | 3766 | 0x03,0x06,0x10 | Y | 1 |  | 0 - Disable 1 - Enable
Permissive Starts | UINT16 | 2 | 1 | 1 | 30 | 1 | 1 | RW | 43768 | 3768 | 3767 | 0x03,0x06,0x10 | Y | 6
Reference time | UINT16 | 2 | 1 | 15 | 60 | 1 | 1 | RW | 43769 | 3769 | 3768 | 0x03,0x06,0x10 | Y | 30 | Minutes
Inhibit Period | UINT16 | 2 | 1 | 1 | 120 | 1 | 1 | RW | 43770 | 3770 | 3769 | 0x03,0x06,0x10 | Y | 5 | Minutes
Time Between Starts | UINT16 | 2 | 1 | 0 | 120 | 1 | 1 | RW | 43771 | 3771 | 3770 | 0x03,0x06,0x10 | Y | 0 | Minutes
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43772 | 3772 | 3771 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43773 | 3773 | 3772 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43774 | 3774 | 3773 | 0x03,0x06,0x10 | N | 0
Motor stop error detection
Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43775 | 3775 | 3774 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43776 | 3776 | 3775 | 0x03,0x06,0x10 | Y | 10 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 7 | 1 | 1 | RW | 43777 | 3777 | 3776 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43778 | 3778 | 3777 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43779 | 3779 | 3778 | 0x03,0x06,0x10 | N | 0
Device Internal
Function | UINT16 | 2 | 1 | 1 | 1 | 1 | 1 | RW | 43780 | 3780 | 3779 | 0x03,0x06,0x10 | Y | 1 |  | 1 - Enable | Configuration error, CT communication loss, Exp comm loss, Internal temperature
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43781 | 3781 | 3780 | 0x03,0x06,0x10 | Y | 10 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 7 | 1 | 1 | RW | 43782 | 3782 | 3781 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication
Reserved | UINT16 | 2 | 1 | 0 | 1 | 0 | 0 | RW | 43783 | 3783 | 3782 | 0x03,0x06,0x12 | N | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43784 | 3784 | 3783 | 0x03,0x06,0x10 | N | 0
Communication loss
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43785 | 3785 | 3784 | 0x03,0x06,0x10 | Y | 3 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43786 | 3786 | 3785 | 0x03,0x06,0x10 | Y | 10 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43787 | 3787 | 3786 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43788 | 3788 | 3787 | 0x03,0x06,0x10 | Y | 0 | Seconds
Trip in Remote mode only | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43789 | 3789 | 3788 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Temperature (Main Unit)
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43790 | 3790 | 3789 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
PT100 Pickup | UINT16 | 2 | 1 | 250 | 1800 | 10 | 1/10 | RW | 43791 | 3791 | 3790 | 0x03,0x06,0x10 | Y | 1300 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | 770 | 3560 | 10 | 1/10 | [7 empty] | F | Refer Min max values as per the unit selected for temperature measurement
PTC Pickup | UINT16 | 2 | 1 | 2700 | 4000 | 1 | 1 | RW | 43792 | 3792 | 3791 | 0x03,0x06,0x10 | Y | 2700 | Ohm
PTC Pickup Reset | UINT16 | 2 | 1 | 1600 | 2300 | 1 | 1 | RW | 43793 | 3793 | 3792 | 0x03,0x06,0x10 | Y | 1600 | Ohm
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43794 | 3794 | 3793 | 0x03,0x06,0x10 | Y | 10 | Seconds
PT100 Alarm Level | UINT16 | 2 | 1 | 250 | 1800 | 10 | 1/10 | RW | 43795 | 3795 | 3794 | 0x03,0x06,0x10 | Y | 1300 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | 770 | 3560 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43796 | 3796 | 3795 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43797 | 3797 | 3796 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43798 | 3798 | 3797 | 0x03,0x06,0x10 | N | 0
Block Output
Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43799 | 3799 | 3798 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Contactor/Braker Open Time | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/100 | RW | 43800 | 3800 | 3799 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43801 | 3801 | 3800 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43802 | 3802 | 3801 | 0x03,0x06,0x10 | N | 0
Anti backspin timer
Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 43803 | 3803 | 3802 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Time Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1 | RW | 43804 | 3804 | 3803 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43805 | 3805 | 3804 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43806 | 3806 | 3805 | 0x03,0x06,0x10 | N | 0
HMI Communication loss
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43807 | 3807 | 3806 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 43808 | 3808 | 3807 | 0x03,0x06,0x10 | Y | 10 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43809 | 3809 | 3808 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43810 | 3810 | 3809 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43811 | 3811 | 3810 | 0x03,0x06,0x10 | N | 0
DI Interlock Protections
DI 1
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43876 | 3876 | 3875 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43877 | 3877 | 3876 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43878 | 3878 | 3877 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43879 | 3879 | 3878 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43880 | 3880 | 3879 | 0x03,0x06,0x10 | N | 0
DI 2
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43881 | 3881 | 3880 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43882 | 3882 | 3881 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43883 | 3883 | 3882 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43884 | 3884 | 3883 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43885 | 3885 | 3884 | 0x03,0x06,0x10 | N | 0
DI 3
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43886 | 3886 | 3885 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43887 | 3887 | 3886 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43888 | 3888 | 3887 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43889 | 3889 | 3888 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43890 | 3890 | 3889 | 0x03,0x06,0x10 | N | 0
DI 4
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43891 | 3891 | 3890 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43892 | 3892 | 3891 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43893 | 3893 | 3892 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43894 | 3894 | 3893 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43895 | 3895 | 3894 | 0x03,0x06,0x10 | N | 0
DI 5
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43896 | 3896 | 3895 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43897 | 3897 | 3896 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43898 | 3898 | 3897 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43899 | 3899 | 3898 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43900 | 3900 | 3899 | 0x03,0x06,0x10 | N | 0
DI 6
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43901 | 3901 | 3900 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43902 | 3902 | 3901 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43903 | 3903 | 3902 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43904 | 3904 | 3903 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43905 | 3905 | 3904 | 0x03,0x06,0x10 | N | 0
DI 7
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43906 | 3906 | 3905 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43907 | 3907 | 3906 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43908 | 3908 | 3907 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43909 | 3909 | 3908 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43910 | 3910 | 3909 | 0x03,0x06,0x10 | N | 0
DI 8
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43911 | 3911 | 3910 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43912 | 3912 | 3911 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43913 | 3913 | 3912 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43914 | 3914 | 3913 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43915 | 3915 | 3914 | 0x03,0x06,0x10 | N | 0
DI 9
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43916 | 3916 | 3915 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43917 | 3917 | 3916 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43918 | 3918 | 3917 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43919 | 3919 | 3918 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43920 | 3920 | 3919 | 0x03,0x06,0x10 | N | 0
DI 10
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43921 | 3921 | 3920 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43922 | 3922 | 3921 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43923 | 3923 | 3922 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43924 | 3924 | 3923 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43925 | 3925 | 3924 | 0x03,0x06,0x10 | N | 0
DI 11
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43926 | 3926 | 3925 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43927 | 3927 | 3926 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43928 | 3928 | 3927 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43929 | 3929 | 3928 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43930 | 3930 | 3929 | 0x03,0x06,0x10 | N | 0
DI 12
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 43931 | 3931 | 3930 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43932 | 3932 | 3931 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 43933 | 3933 | 3932 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 43934 | 3934 | 3933 | 0x03,0x06,0x10 | Y | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 43935 | 3935 | 3934 | 0x03,0x06,0x10 | N | 0
AI Protections
AI 1
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44001 | 4001 | 4000 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Detection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44002 | 4002 | 4001 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Under 1 - Over
Pickup | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44003 | 4003 | 4002 | 0x03,0x06,0x10 | Y | 40 | mA
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44004 | 4004 | 4003 | 0x03,0x06,0x10 | Y | 0 | Seconds
Alarm | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44005 | 4005 | 4004 | 0x03,0x06,0x10 | Y | 40 | mA
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44006 | 4006 | 4005 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44007 | 4007 | 4006 | 0x03,0x06,0x10 | Y | 0 | Seconds
reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44008 | 4008 | 4007 | 0x03,0x06,0x10 | Y | 0
AI 2
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44009 | 4009 | 4008 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Detection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44010 | 4010 | 4009 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Under 1 - Over
Pickup | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44011 | 4011 | 4010 | 0x03,0x06,0x10 | Y | 40 | mA
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44012 | 4012 | 4011 | 0x03,0x06,0x10 | Y | 0 | Seconds
Alarm | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44013 | 4013 | 4012 | 0x03,0x06,0x10 | Y | 40 | mA
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44014 | 4014 | 4013 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44015 | 4015 | 4014 | 0x03,0x06,0x10 | Y | 0 | Seconds
reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44016 | 4016 | 4015 | 0x03,0x06,0x10 | Y | 0
AI 3
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44017 | 4017 | 4016 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Detection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44018 | 4018 | 4017 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Under 1 - Over
Pickup | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44019 | 4019 | 4018 | 0x03,0x06,0x10 | Y | 40 | mA
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44020 | 4020 | 4019 | 0x03,0x06,0x10 | Y | 0 | Seconds
Alarm | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44021 | 4021 | 4020 | 0x03,0x06,0x10 | Y | 40 | mA
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44022 | 4022 | 4021 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44023 | 4023 | 4022 | 0x03,0x06,0x10 | Y | 0 | Seconds
reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44024 | 4024 | 4023 | 0x03,0x06,0x10 | Y | 0
AI 4
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44025 | 4025 | 4024 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Detection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44026 | 4026 | 4025 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Under 1 - Over
Pickup | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44027 | 4027 | 4026 | 0x03,0x06,0x10 | Y | 40 | mA
Time delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44028 | 4028 | 4027 | 0x03,0x06,0x10 | Y | 0 | Seconds
Alarm | UINT16 | 2 | 1 | 40 | 200 | 1 | 1/10 | RW | 44029 | 4029 | 4028 | 0x03,0x06,0x10 | Y | 40 | mA
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44030 | 4030 | 4029 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44031 | 4031 | 4030 | 0x03,0x06,0x10 | Y | 0 | Seconds
reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44032 | 4032 | 4031 | 0x03,0x06,0x10 | Y | 0
Temperature Protections
TI 1
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44126 | 4126 | 4125 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44127 | 4127 | 4126 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44128 | 4128 | 4127 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44129 | 4129 | 4128 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44130 | 4130 | 4129 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44131 | 4131 | 4130 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44132 | 4132 | 4131 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44133 | 4133 | 4132 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 2
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44134 | 4134 | 4133 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44135 | 4135 | 4134 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44136 | 4136 | 4135 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44137 | 4137 | 4136 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44138 | 4138 | 4137 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44139 | 4139 | 4138 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44140 | 4140 | 4139 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44141 | 4141 | 4140 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 3
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44142 | 4142 | 4141 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44143 | 4143 | 4142 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44144 | 4144 | 4143 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44145 | 4145 | 4144 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44146 | 4146 | 4145 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44147 | 4147 | 4146 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44148 | 4148 | 4147 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44149 | 4149 | 4148 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 4
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44150 | 4150 | 4149 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44151 | 4151 | 4150 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44152 | 4152 | 4151 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44153 | 4153 | 4152 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44154 | 4154 | 4153 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44155 | 4155 | 4154 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44156 | 4156 | 4155 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44157 | 4157 | 4156 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 5
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44158 | 4158 | 4157 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44159 | 4159 | 4158 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44160 | 4160 | 4159 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44161 | 4161 | 4160 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44162 | 4162 | 4161 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44163 | 4163 | 4162 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44164 | 4164 | 4163 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44165 | 4165 | 4164 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 6
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44166 | 4166 | 4165 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44167 | 4167 | 4166 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44168 | 4168 | 4167 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44169 | 4169 | 4168 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44170 | 4170 | 4169 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44171 | 4171 | 4170 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44172 | 4172 | 4171 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44173 | 4173 | 4172 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 7
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44174 | 4174 | 4173 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44175 | 4175 | 4174 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44176 | 4176 | 4175 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44177 | 4177 | 4176 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44178 | 4178 | 4177 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44179 | 4179 | 4178 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44180 | 4180 | 4179 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44181 | 4181 | 4180 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 8
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44182 | 4182 | 4181 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44183 | 4183 | 4182 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44184 | 4184 | 4183 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44185 | 4185 | 4184 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44186 | 4186 | 4185 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44187 | 4187 | 4186 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44188 | 4188 | 4187 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44189 | 4189 | 4188 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 9
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44190 | 4190 | 4189 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44191 | 4191 | 4190 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44192 | 4192 | 4191 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44193 | 4193 | 4192 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44194 | 4194 | 4193 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44195 | 4195 | 4194 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44196 | 4196 | 4195 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44197 | 4197 | 4196 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 10
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44198 | 4198 | 4197 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44199 | 4199 | 4198 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44200 | 4200 | 4199 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44201 | 4201 | 4200 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44202 | 4202 | 4201 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44203 | 4203 | 4202 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44204 | 4204 | 4203 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44205 | 4205 | 4204 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 11
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44206 | 4206 | 4205 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44207 | 4207 | 4206 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44208 | 4208 | 4207 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44209 | 4209 | 4208 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44210 | 4210 | 4209 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44211 | 4211 | 4210 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44212 | 4212 | 4211 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44213 | 4213 | 4212 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 12
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44214 | 4214 | 4213 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44215 | 4215 | 4214 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44216 | 4216 | 4215 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44217 | 4217 | 4216 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44218 | 4218 | 4217 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44219 | 4219 | 4218 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44220 | 4220 | 4219 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44221 | 4221 | 4220 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 13
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44222 | 4222 | 4221 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44223 | 4223 | 4222 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44224 | 4224 | 4223 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44225 | 4225 | 4224 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44226 | 4226 | 4225 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44227 | 4227 | 4226 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44228 | 4228 | 4227 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44229 | 4229 | 4228 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 14
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44230 | 4230 | 4229 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44231 | 4231 | 4230 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44232 | 4232 | 4231 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44233 | 4233 | 4232 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44234 | 4234 | 4233 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44235 | 4235 | 4234 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44236 | 4236 | 4235 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44237 | 4237 | 4236 | 0x03,0x06,0x10 | Y | 0 | Seconds
TI 15
Function | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44238 | 4238 | 4237 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Alarm 2 - Trip 3 - Alarm +Trip
Temp Pickup | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44239 | 4239 | 4238 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Diagnostic | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44240 | 4240 | 4239 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Disable 1 - Enable
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44241 | 4241 | 4240 | 0x03,0x06,0x10 | N | 0
Time Delay | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/10 | RW | 44242 | 4242 | 4241 | 0x03,0x06,0x10 | Y | 10 | Seconds
Temp Alarm Level | INT16 | 2 | 1 | -50 | 500 | 1 | 1 | RW | 44243 | 4243 | 4242 | 0x03,0x06,0x10 | Y | 130 | °C | Refer Min max values as per the unit selected for temperature measurement
|  |  |  | -58 | 932 | [9 empty] | F | Refer Min max values as per the unit selected for temperature measurement
Reset Mode | BITMAP | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44244 | 4244 | 4243 | 0x03,0x06,0x10 | Y | 3 |  | Bit 0 - Reset Key Bit 1 - DI Bit 2 - Communication Bit 3 - Auto
Auto-Reset Delay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 44245 | 4245 | 4244 | 0x03,0x06,0x10 | Y | 0 | Seconds
Misc. Settings
Hysteresis Settings
Current Protection | UINT16 | 2 | 1 | 3 | 15 | 1 | 1 | RW | 44251 | 4251 | 4250 | 0x03,0x06,0x10 | Y | 3 | %
Voltage Protection | UINT16 | 2 | 1 | 3 | 15 | 1 | 1 | RW | 44252 | 4252 | 4251 | 0x03,0x06,0x10 | Y | 3 | %
Frequency Protection | UINT16 | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44253 | 4253 | 4252 | 0x03,0x06,0x10 | Y | 3 | %
Power Protection | UINT16 | 2 | 1 | 3 | 15 | 1 | 1 | RW | 44254 | 4254 | 4253 | 0x03,0x06,0x10 | Y | 3 | %
Analog Input Protection | UINT16 | 2 | 1 | 1 | 3 | 1 | 1 | RW | 44255 | 4255 | 4254 | 0x03,0x06,0x10 | Y | 1 | mA
Temperature Protection | UINT16 | 2 | 1 | 2 | 15 | 1 | 1 | RW | 44256 | 4256 | 4255 | 0x03,0x06,0x10 | Y | 5 | °C
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44257 | 4257 | 4256 | 0x03,0x06,0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44258 | 4258 | 4257 | 0x03,0x06,0x10 | Y | 0
Fallback setting
Source | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44259 | 4259 | 4258 | 0x03,0x06,0x10 | Y | 0 |  | 0:None 1: Communication loss 2: HMI communication loss 3: Both
DO1 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44260 | 4260 | 4259 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO2 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44261 | 4261 | 4260 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO3 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44262 | 4262 | 4261 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO4 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44263 | 4263 | 4262 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO5 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44264 | 4264 | 4263 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO6 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44265 | 4265 | 4264 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO7 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44266 | 4266 | 4265 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO8 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44267 | 4267 | 4266 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO9 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44268 | 4268 | 4267 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO10 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44269 | 4269 | 4268 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO11 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44270 | 4270 | 4269 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO12 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44271 | 4271 | 4270 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
DO13 State | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44272 | 4272 | 4271 | 0x03,0x06,0x10 | Y | 0 |  | 0: OFF 1: HOLD 2: ON
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44273 | 4273 | 4272 | 0x03,0x06,0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44274 | 4274 | 4273 | 0x03,0x06,0x10 | Y | 0
Note on F240: Vrund Rana: range is 770 -3560 in fahrenheit

## General Settings
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Device Configuration
Sensor Module Type | UINT16 | 2 | 1 | 1 | 15 | 1 | 1 | RW | 44376 | 4376 | 4375 | 0x03,0x06,0x10 | Y | 8 |  | 1 - LTMTCT3L 2 - LTMTCTV3L 3 - LTMTCT3T 4 - LTMTCTV3T 5 - LTMTCT25L 6 - LTMTCTV25L 7 - LTMTCT25T 8 - LTMTCTV25T 9 - LTMTCT70L 10 - LTMTCTV70L 11 - LTMTCT100T 12 - LTMTCTV100T 13 - LTMTCTV3UT 14 - LTMTCTV25UT 15 - LTMTCTV100UT
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44377 | 4377 | 4376 | 0x03,0x06,0x10 | Y | 0
Expansion Module 1 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | RW | 44378 | 4378 | 4377 | 0x03,0x06,0x10 | Y | 0 |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 1 Setting | UINT16 | 2 | 1 | 0 | 10 | 1 | 1 | RW | 44379 | 4379 | 4378 | 0x03,0x06,0x10 | Y | 2 |  | 0 to 1 - For future use Applicable Only for Temperature Module: 2 - PT100 3 - PT1000 4 - KTY83 5 - KTY84 6 - NTC 7- PTC 8 to 10 - For future use
Expansion Module 2 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | RW | 44380 | 4380 | 4379 | 0x03,0x06,0x10 | Y | 0 |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 2 Setting | UINT16 | 2 | 1 | 0 | 10 | 1 | 1 | RW | 44381 | 4381 | 4380 | 0x03,0x06,0x10 | Y | 2 |  | 0 to 1 - For future use Applicable Only for Temperature Module: 2 - PT100 3 - PT1000 4 - KTY83 5 - KTY84 6 - NTC 7- PTC 8 to 10 - For future use
Expansion Module 3 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | RW | 44382 | 4382 | 4381 | 0x03,0x06,0x10 | Y | 0 |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 3 Setting | UINT16 | 2 | 1 | 0 | 10 | 1 | 1 | RW | 44383 | 4383 | 4382 | 0x03,0x06,0x10 | Y | 2 |  | 0 to 1 - For future use Applicable Only for Temperature Module: 2 - PT100 3 - PT1000 4 - KTY83 5 - KTY84 6 - NTC 7- PTC 8 to 10 - For future use
Expansion Module 4 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | RW | 44384 | 4384 | 4383 | 0x03,0x06,0x10 | Y | 0 |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 4 Setting | UINT16 | 2 | 1 | 0 | 10 | 1 | 1 | RW | 44385 | 4385 | 4384 | 0x03,0x06,0x10 | Y | 2 |  | 0 to 1 - For future use Applicable Only for Temperature Module: 2 - PT100 3 - PT1000 4 - KTY83 5 - KTY84 6 - NTC 7- PTC 8 to 10 - For future use
Expansion Module 5 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | RW | 44386 | 4386 | 4385 | 0x03,0x06,0x10 | Y | 0 |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 5 Setting | UINT16 | 2 | 1 | 0 | 10 | 1 | 1 | RW | 44387 | 4387 | 4386 | 0x03,0x06,0x10 | Y | 2 |  | 0 to 1 - For future use Applicable Only for Temperature Module: 2 - PT100 3 - PT1000 4 - KTY83 5 - KTY84 6 - NTC 7- PTC 8 to 10 - For future use
Main Unit Temperature | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44388 | 4388 | 4387 | 0x03,0x06,0x10 | Y | 0 |  | 0 - None 1 - PT100 2 - PTC
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44389 | 4389 | 4388 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44390 | 4390 | 4389 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44391 | 4391 | 4390 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44392 | 4392 | 4391 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44393 | 4393 | 4392 | 0x03,0x06,0x10 | N | 0
Modbus Settings Not Applicable for Ethernet (Reserved bytes in case of Ethernet Variants)
Node Address | UINT16 | 2 | 1 | 1 | 247 | 1 | 1 | RW | 44394 | 4394 | 4393 | 0x03,0x10 | Y | 1
Parity | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44395 | 4395 | 4394 | 0x03,0x10 | Y | 2 |  | 0 = None 1 = ODD 2 = EVEN
Baud Rate | UINT16 | 2 | 1 | 0 | 6 | 1 | 1 | RW | 44396 | 4396 | 4395 | 0x03,0x10 | Y | 3 |  | 0 = 2400 1 = 4800 2 = 9600 3= 19200 4 = 38400 5 = 57600 6 = 115200
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44397 | 4397 | 4396 | 0x03,0x10 | N | 0
Timeout | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1 | RW | 44398 | 4398 | 4397 | 0x03,0x10 | Y | 1 | Seconds
Byte Format | BITMAP | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44399 | 4399 | 4398 | 0x03,0x10 | Y | 0 |  | Bit 0: 0: Big Endian 1: Little Endian
HMI Settings
Node Address | UINT16 | 2 | 1 | 1 | 247 | 1 | 1 | RW | 44400 | 4400 | 4399 | 0x03,0x10 | Y | 1
Parity | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44401 | 4401 | 4400 | 0x03,0x10 | Y | 2 |  | 0 = None 1 = ODD 2 = EVEN
Baud Rate | UINT16 | 2 | 1 | 0 | 6 | 1 | 1 | RW | 44402 | 4402 | 4401 | 0x03,0x10 | Y | 3 |  | 0 = 2400 1 = 4800 2 = 9600 3= 19200 4 = 38400 5 = 57600 6 = 115200
Control Keys | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44403 | 4403 | 4402 | 0x03,0x10 | N | 0 |  | 0 - Default 1 - Programmable
Timeout | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1 | RW | 44404 | 4404 | 4403 | 0x03,0x10 | Y | 1 | Seconds
Byte Format | BITMAP | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44405 | 4405 | 4404 | 0x03,0x10 | Y | 0 |  | Bit 0: 0: Big Endian 1: Little Endian
Profibus Settings: Not Applicable for Ethernet (Reserved bytes in case of Ethernet Variants)
Node Address | UINT16 | 2 | 1 | 2 | 126 | 1 | 1 | RW | 44406 | 4406 | 4405 | 0x03,0x06,0x10 | Y | 126
Endian | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44407 | 4407 | 4406 | 0x03,0x06,0x10 | Y | 0
Product Profile | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44408 | 4408 | 4407 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Default 1 - TeSys T 2 - Other
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44409 | 4409 | 4408 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44410 | 4410 | 4409 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44411 | 4411 | 4410 | 0x03,0x06,0x10 | N | 0
Date & Time Settings
Date | UINT16 | 2 | 1 | 1 | 31 | 1 | 1 | RW | 44412 | 4412 | 4411 | 0x03, 0x10 | Y | 1
Month | UINT16 | 2 | 1 | 1 | 12 | 1 | 1 | RW | 44413 | 4413 | 4412 | 0x03, 0x10 | Y | 1
Year | UINT16 | 2 | 1 | 2000 | 2999 | 1 | 1 | RW | 44414 | 4414 | 4413 | 0x03, 0x10 | Y | 2024
Hour | UINT16 | 2 | 1 | 0 | 23 | 1 | 1 | RW | 44415 | 4415 | 4414 | 0x03, 0x10 | Y | 0
Minute | UINT16 | 2 | 1 | 0 | 59 | 1 | 1 | RW | 44416 | 4416 | 4415 | 0x03, 0x10 | Y | 0
Second | UINT16 | 2 | 1 | 0 | 59 | 1 | 1 | RW | 44417 | 4417 | 4416 | 0x03, 0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44418 | 4418 | 4417 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44419 | 4419 | 4418 | 0x03, 0x10 | N | 0
Apply Date & Time | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44420 | 4420 | 4419 | 0x03, 0x10 | N | 0
Starter Settings
Load type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44421 | 4421 | 4420 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Motor 1 - Heater
Starter Type | UINT16 | 2 | 1 | 0 | 511 | 1 | 1 | RW | 44422 | 4422 | 4421 | 0x03,0x06,0x10 | Y | 1 |  | Refer Table 2
Mode Selection | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44423 | 4423 | 4422 | 0x03,0x06,0x10 | Y | 0
Local 1 Start | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44424 | 4424 | 4423 | 0x03,0x06,0x10 | Y | 11 |  | Refer Table 1
Local 2 Start | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44425 | 4425 | 4424 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 1
Local 3 Start | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44426 | 4426 | 4425 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 1
Remote Start | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44427 | 4427 | 4426 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 1
Local 1 Stop | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44428 | 4428 | 4427 | 0x03,0x06,0x10 | Y | 11 |  | Refer Table 1
Local 2 Stop | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44429 | 4429 | 4428 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 1
Local 3 Stop | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44430 | 4430 | 4429 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 1
Remote Stop | UINT16 | 2 | 1 | 0 | 31 | 1 | 1 | RW | 44431 | 4431 | 4430 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 1
Local DI Start Input | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44432 | 4432 | 4431 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Momentary 1 - Maintained
Remote DI Start Input | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44433 | 4433 | 4432 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Momentary 1 - Maintained
Custom Start Input | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44434 | 4434 | 4433 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Momentary 1 - Maintained
Mode Transfer | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44435 | 4435 | 4434 | 0x03,0x06,0x10 | N | 0 |  | 0 - Bump 1 - Bumpless
Communication Start Input | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44436 | 4436 | 4435 | 0x03,0x06,0x10 | Y | 0 |  | 0 - Momentary 1 - Maintained
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44437 | 4437 | 4436 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44438 | 4438 | 4437 | 0x03,0x06,0x10 | N | 0
Change Direction | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44439 | 4439 | 4438 | 0x03,0x06,0x10 | Y | 0 |  | 0: Disable 1: Enable
Feedback Response Time | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44440 | 4440 | 4439 | 0x03,0x06,0x10 | Y | 50 | Seconds
Motor Current Sensing Time | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44441 | 4441 | 4440 | 0x03,0x06,0x10 | Y | 50 | Seconds
Interlocking Time | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44442 | 4442 | 4441 | 0x03,0x06,0x10 | Y | 6000 | Seconds
Delay 1 | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44443 | 4443 | 4442 | 0x03,0x06,0x10 | Y | 1000 | Seconds | Refer Table 2
Delay 2 | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44444 | 4444 | 4443 | 0x03,0x06,0x10 | Y | 30 | Seconds | Refer Table 2
Delay 3 | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44445 | 4445 | 4444 | 0x03,0x06,0x10 | Y | 1 | Seconds | Refer Table 2
Delay 4 | UINT16 | 2 | 1 | 1 | 60000 | 1 | 1/100 | RW | 44446 | 4446 | 4445 | 0x03,0x06,0x10 | Y | 1 | Seconds | Refer Table 2
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44447 | 4447 | 4446 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44448 | 4448 | 4447 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44449 | 4449 | 4448 | 0x03,0x06,0x10 | N | 0
Number of Phases | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44450 | 4450 | 4449 | 0x03,0x06,0x10 | Y | 0 |  | 0: Three Phase 1: Single Phase
Stop Detection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44451 | 4451 | 4450 | 0x03,0x06,0x10 | Y | 1 |  | 0: DI + Current Based 1: Current Based
Forced start function | UINT16 | 2 | 1 | 0 | 1 | 0 | 1 | RW | 44452 | 4452 | 4451 | 0x03,0x06,0x10 | Y | 0 |  | 0: Disable 1: Enable
System Settings
Phase CT Primary | UINT16 | 2 | 1 | 1 | 1000 | 1 | 1 | RW | 44453 | 4453 | 4452 | 0x03,0x10 | Y | 1 | Amp
Phase CT Secondary | UINT16 | 2 | 1 | 1 | 5 | 4 | 1 | RW | 44454 | 4454 | 4453 | 0x03,0x10 | Y | 1 | Amp
Reserved | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44455 | 4455 | 4454 | 0x03,0x10 | Y | 1
Reserved | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44456 | 4456 | 4455 | 0x03,0x10 | Y | 1
Speed 2 CT primary | UINT16 | 2 | 1 | 1 | 1000 | 1 | 1 | RW | 44457 | 4457 | 4456 | 0x03,0x10 | Y | 1 | Amp
Speed 2 CT secondary | UINT16 | 2 | 1 | 1 | 5 | 4 | 1 | RW | 44458 | 4458 | 4457 | 0x03,0x10 | Y | 1 | Amp
Reserved | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44459 | 4459 | 4458 | 0x03,0x10 | Y | 1
Reserved | UINT16 | 2 | 1 | 0 | 1 | 4 | 1 | RW | 44460 | 4460 | 4459 | 0x03,0x10 | Y | 1
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44461 | 4461 | 4460 | 0x03,0x10 | Y | 0
Voltage Nominal | UINT16 | 2 | 1 | 1100 | 6900 | 1 | 1/10 | RW | 44462 | 4462 | 4461 | 0x03,0x10 | Y | 4150 | V
Nominal Frequency | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44463 | 4463 | 4462 | 0x03,0x10 | Y | 0 |  | 0: 50Hz 1: 60Hz
Phase rotation | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44464 | 4464 | 4463 | 0x03,0x10 | Y | 0 |  | 0: L123 1: L132
Voltage Input | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44465 | 4465 | 4464 | 0x03,0x10 | Y | 1 |  | 0: Disable 1: Enable Applicable only for CTVT variant, if disable Tesys Tera will not provide voltage protections and inhibits
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44466 | 4466 | 4465 | 0x03,0x10 | N | 0
Full load Current | UINT16 | 2 | 1 | 1 | 10000 | 1 | 1/10 | RW | 44467 | 4467 | 4466 | 0x03,0x10 | Y | 25 | Amp
Speed 2 Full Load Current | UINT16 | 2 | 1 | 1 | 10000 | 1 | 1/10 | RW | 44468 | 4468 | 4467 | 0x03,0x10 | Y | 25 | Amp
Phase CT secondary passes | UINT16 | 2 | 1 | 1 | 10 | 1 | 1 | RW | 44469 | 4469 | 4468 | 0x03,0x10 | N | 1
Speed 2 phase secondary passes | UINT16 | 2 | 1 | 1 | 10 | 1 | 1 | RW | 44470 | 4470 | 4469 | 0x03,0x10 | N | 1
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44471 | 4471 | 4470 | 0x03,0x10 | N | 0 | Seconds
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44472 | 4472 | 4471 | 0x03,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44473 | 4473 | 4472 | 0x03,0x10 | N | 0
Test Mode | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44474 | 4474 | 4473 | 0x03,0x10 | Y | 1 |  | 0: Disable 1: Enable
Bypass Interlocks during test | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44475 | 4475 | 4474 | 0x03,0x10 | Y | 0 |  | 0: No 1: Yes
Motor Name Plate Details
User Application Name(Modbus TCP/ EIP) same can not be used for Profinet as character limitation and access level is also there Must be used for FDR | ASCII | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 44476 | 4476 | 4475 | 0x03,0x06,0x10 | Y | 0x4D4D, 0x5230, 0x3030, 0x3030, 0x3031 |  | Motor Tag values should be in ASCII
Power Unit | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44481 | 4481 | 4480 | 0x03,0x06,0x10 | Y | 0 |  | 0:kW 1:HP
Nominal Power (KW) | UINT16 | 2 | 1 | 1 | 65535 | 1 | 1/10 | RW | 44482 | 4482 | 4481 | 0x03,0x06,0x10 | Y | 1 | kW | Based on HP value KW has to be computed at DTM
Nominal Power (HP) | UINT16 | 2 | 1 | 1 | 65535 | 1 | 1/10 | RW | 44483 | 4483 | 4482 | 0x03,0x06,0x10 | Y | 1 | HP | Based on KW value HP has to be computed at DTM
Temperature Unit | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44484 | 4484 | 4483 | 0x03,0x06,0x10 | Y | 0 |  | 0: °C 1: Fahrenheit
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44485 | 4485 | 4484 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44486 | 4486 | 4485 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44487 | 4487 | 4486 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44488 | 4488 | 4487 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44489 | 4489 | 4488 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44490 | 4490 | 4489 | 0x03,0x06,0x10 | N | 0
Session Management
Session Timeout | UINT16 | 2 | 1 | 5 | 60 | 1 | 1 | RW | 44491 | 4491 | 4490 | 0x03,0x06,0x10 | Y | 15 | Minutes
Reserved | UINT16 | 18 | 9 | 0 | 0 | 0 | 0 | RW | 44492 | 4492 | 4491 | 0x03,0x06,0x10 | N | 0
DI Settings
DI1 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44501 | 4501 | 4500 | 0x03,0x06,0x10 | Y | anis |  | 0: Active High 1: Active Low
DI1 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44502 | 4502 | 4501 | 0x03,0x06,0x10 | Y | 4 |  | Refer Table 3
DI1 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44503 | 4503 | 4502 | 0x03,0x06,0x10 | Y | 10 | mSec
DI2 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44504 | 4504 | 4503 | 0x03,0x06,0x10 | Y | 1 |  | 0: Active High 1: Active Low
DI2 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44505 | 4505 | 4504 | 0x03,0x06,0x10 | Y | 6 |  | Refer Table 3
DI2 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44506 | 4506 | 4505 | 0x03,0x06,0x10 | Y | 10 | mSec
DI3 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44507 | 4507 | 4506 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI3 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44508 | 4508 | 4507 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI3 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44509 | 4509 | 4508 | 0x03,0x06,0x10 | Y | 10 | mSec
DI4 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44510 | 4510 | 4509 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI4 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44511 | 4511 | 4510 | 0x03,0x06,0x10 | Y | 30 |  | Refer Table 3
DI4 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44512 | 4512 | 4511 | 0x03,0x06,0x10 | Y | 10 | mSec
DI5 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44513 | 4513 | 4512 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI5 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44514 | 4514 | 4513 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI5 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44515 | 4515 | 4514 | 0x03,0x06,0x10 | Y | 10 | mSec
DI6 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44516 | 4516 | 4515 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI6 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44517 | 4517 | 4516 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI6 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44518 | 4518 | 4517 | 0x03,0x06,0x10 | Y | 10 | mSec
DI7 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44519 | 4519 | 4518 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI7 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44520 | 4520 | 4519 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI7 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44521 | 4521 | 4520 | 0x03,0x06,0x10 | Y | 10 | mSec
DI8 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44522 | 4522 | 4521 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI8 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44523 | 4523 | 4522 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI8 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44524 | 4524 | 4523 | 0x03,0x06,0x10 | Y | 10 | mSec
DI9 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44525 | 4525 | 4524 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI9 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44526 | 4526 | 4525 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI9 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44527 | 4527 | 4526 | 0x03,0x06,0x10 | Y | 10 | mSec
DI10 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44528 | 4528 | 4527 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI10 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44529 | 4529 | 4528 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI10 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44530 | 4530 | 4529 | 0x03,0x06,0x10 | Y | 10 | mSec
DI11 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44531 | 4531 | 4530 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI11 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44532 | 4532 | 4531 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI11 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44533 | 4533 | 4532 | 0x03,0x06,0x10 | Y | 10 | mSec
DI12 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44534 | 4534 | 4533 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI12 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44535 | 4535 | 4534 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI12 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44536 | 4536 | 4535 | 0x03,0x06,0x10 | Y | 10 | mSec
DI13 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44537 | 4537 | 4536 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI13 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44538 | 4538 | 4537 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI13 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44539 | 4539 | 4538 | 0x03,0x06,0x10 | Y | 10 | mSec
DI14 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44540 | 4540 | 4539 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI14 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44541 | 4541 | 4540 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI14 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44542 | 4542 | 4541 | 0x03,0x06,0x10 | Y | 10 | mSec
DI15 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44543 | 4543 | 4542 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI15 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44544 | 4544 | 4543 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI15 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44545 | 4545 | 4544 | 0x03,0x06,0x10 | Y | 10 | mSec
DI16 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44546 | 4546 | 4545 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI16 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44547 | 4547 | 4546 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI16 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44548 | 4548 | 4547 | 0x03,0x06,0x10 | Y | 10 | mSec
DI17 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44549 | 4549 | 4548 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI17 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44550 | 4550 | 4549 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI17 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44551 | 4551 | 4550 | 0x03,0x06,0x10 | Y | 10 | mSec
DI18 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44552 | 4552 | 4551 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI18 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44553 | 4553 | 4552 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI18 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44554 | 4554 | 4553 | 0x03,0x06,0x10 | Y | 10 | mSec
DI19 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44555 | 4555 | 4554 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI19 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44556 | 4556 | 4555 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI19 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44557 | 4557 | 4556 | 0x03,0x06,0x10 | Y | 10 | mSec
DI20 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44558 | 4558 | 4557 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI20 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44559 | 4559 | 4558 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI20 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44560 | 4560 | 4559 | 0x03,0x06,0x10 | Y | 10 | mSec
DI21 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44561 | 4561 | 4560 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI21 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44562 | 4562 | 4561 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI21 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44563 | 4563 | 4562 | 0x03,0x06,0x10 | Y | 10 | mSec
DI22 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44564 | 4564 | 4563 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI22 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44565 | 4565 | 4564 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI22 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44566 | 4566 | 4565 | 0x03,0x06,0x10 | Y | 10 | mSec
DI23 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44567 | 4567 | 4566 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI23 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44568 | 4568 | 4567 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI23 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44569 | 4569 | 4568 | 0x03,0x06,0x10 | Y | 10 | mSec
DI24 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44570 | 4570 | 4569 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI24 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44571 | 4571 | 4570 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI24 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44572 | 4572 | 4571 | 0x03,0x06,0x10 | Y | 10 | mSec
DI25 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44573 | 4573 | 4572 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI25 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44574 | 4574 | 4573 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI25 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44575 | 4575 | 4574 | 0x03,0x06,0x10 | Y | 10 | mSec
DI26 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44576 | 4576 | 4575 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI26 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44577 | 4577 | 4576 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI26 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44578 | 4578 | 4577 | 0x03,0x06,0x10 | Y | 10 | mSec
DI27 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44579 | 4579 | 4578 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI27 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44580 | 4580 | 4579 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI27 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44581 | 4581 | 4580 | 0x03,0x06,0x10 | Y | 10 | mSec
DI28Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44582 | 4582 | 4581 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI28 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44583 | 4583 | 4582 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI28 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44584 | 4584 | 4583 | 0x03,0x06,0x10 | Y | 10 | mSec
DI29 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44585 | 4585 | 4584 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI29 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44586 | 4586 | 4585 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI29 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44587 | 4587 | 4586 | 0x03,0x06,0x10 | Y | 10 | mSec
DI30 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44588 | 4588 | 4587 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI30 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44589 | 4589 | 4588 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI30 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44590 | 4590 | 4589 | 0x03,0x06,0x10 | Y | 10 | mSec
DI31 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44591 | 4591 | 4590 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI31 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44592 | 4592 | 4591 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI31 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44593 | 4593 | 4592 | 0x03,0x06,0x10 | Y | 10 | mSec
DI32 Trigger Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44594 | 4594 | 4593 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DI32 Input Source | UINT16 | 2 | 1 | 0 | 38 | 1 | 1 | RW | 44595 | 4595 | 4594 | 0x03,0x06,0x10 | Y | 38 |  | Refer Table 3
DI32 Validation Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44596 | 4596 | 4595 | 0x03,0x06,0x10 | Y | 10 | mSec
DO Settings
DO1 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44626 | 4626 | 4625 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO1 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44627 | 4627 | 4626 | 0x03,0x06,0x10 | Y | 504 |  | Refer Comp logic Input list
DO1 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44628 | 4628 | 4627 | 0x03,0x06,0x10 | Y | 7 |  | Refer Table 4
DO1 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44629 | 4629 | 4628 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO1 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44630 | 4630 | 4629 | 0x03,0x06,0x10 | Y | 0 | mSec
DO2 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44631 | 4631 | 4630 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO2 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44632 | 4632 | 4631 | 0x03,0x06,0x10 | Y | 233 |  | Refer Comp logic Input list
DO2 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44633 | 4633 | 4632 | 0x03,0x06,0x10 | Y | 3 |  | Refer Table 4
DO2 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44634 | 4634 | 4633 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO2 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44635 | 4635 | 4634 | 0x03,0x06,0x10 | Y | 0 | mSec
DO3 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44636 | 4636 | 4635 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO3 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44637 | 4637 | 4636 | 0x03,0x06,0x10 | Y | 234 |  | Refer Comp logic Input list
DO3 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44638 | 4638 | 4637 | 0x03,0x06,0x10 | Y | 2 |  | Refer Table 4
DO3 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44639 | 4639 | 4638 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO3 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44640 | 4640 | 4639 | 0x03,0x06,0x10 | Y | 0 | mSec
DO4 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44641 | 4641 | 4640 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO4 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44642 | 4642 | 4641 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO4 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44643 | 4643 | 4642 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO4 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44644 | 4644 | 4643 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO4 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44645 | 4645 | 4644 | 0x03,0x06,0x10 | Y | 0 | mSec
DO5 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44646 | 4646 | 4645 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO5 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44647 | 4647 | 4646 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO5 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44648 | 4648 | 4647 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO5 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44649 | 4649 | 4648 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO5 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44650 | 4650 | 4649 | 0x03,0x06,0x10 | Y | 0 | mSec
DO6 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44651 | 4651 | 4650 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO6 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44652 | 4652 | 4651 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO6 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44653 | 4653 | 4652 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO6 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44654 | 4654 | 4653 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO6 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44655 | 4655 | 4654 | 0x03,0x06,0x10 | Y | 0 | mSec
DO7 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44656 | 4656 | 4655 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO7 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44657 | 4657 | 4656 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO7 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44658 | 4658 | 4657 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO7 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44659 | 4659 | 4658 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO7 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44660 | 4660 | 4659 | 0x03,0x06,0x10 | Y | 0 | mSec
DO8 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44661 | 4661 | 4660 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO8 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44662 | 4662 | 4661 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO8 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44663 | 4663 | 4662 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO8 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44664 | 4664 | 4663 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO8 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44665 | 4665 | 4664 | 0x03,0x06,0x10 | Y | 0 | mSec
DO9 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44666 | 4666 | 4665 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO9 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44667 | 4667 | 4666 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO9 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44668 | 4668 | 4667 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO9 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44669 | 4669 | 4668 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO9 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44670 | 4670 | 4669 | 0x03,0x06,0x10 | Y | 0 | mSec
DO10 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44671 | 4671 | 4670 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO10 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44672 | 4672 | 4671 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO10 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44673 | 4673 | 4672 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO10 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44674 | 4674 | 4673 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO10 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44675 | 4675 | 4674 | 0x03,0x06,0x10 | Y | 0 | mSec
DO11 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44676 | 4676 | 4675 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO11 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44677 | 4677 | 4676 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO11 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44678 | 4678 | 4677 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO11 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44679 | 4679 | 4678 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO11Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44680 | 4680 | 4679 | 0x03,0x06,0x10 | Y | 0 | mSec
DO12 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44681 | 4681 | 4680 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO12 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44682 | 4682 | 4681 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO12 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44683 | 4683 | 4682 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO12 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44684 | 4684 | 4683 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO12 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44685 | 4685 | 4684 | 0x03,0x06,0x10 | Y | 0 | mSec
DO13 Active Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44686 | 4686 | 4685 | 0x03,0x06,0x10 | Y | 0 |  | 0: Active High 1: Active Low
DO13 Input Source | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44687 | 4687 | 4686 | 0x03,0x06,0x10 | Y | 0 |  | Refer Comp logic Input list
DO13 Tag | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44688 | 4688 | 4687 | 0x03,0x06,0x10 | Y | 0 |  | Refer Table 4
DO13 Output Type | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44689 | 4689 | 4688 | 0x03,0x06,0x10 | Y | 0 |  | 0: Level 1: Pulse
DO13 Pulse Time | UINT16 | 2 | 1 | 0 | 60000 | 10 | 1 | RW | 44690 | 4690 | 4689 | 0x03,0x06,0x10 | Y | 0 | mSec
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44691 | 4691 | 4690 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44692 | 4692 | 4691 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44693 | 4693 | 4692 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44694 | 4694 | 4693 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | RW | 44695 | 4695 | 4694 | 0x03,0x06,0x10 | N | 0
AO Settings
AO1 Source | UINT16 | 2 | 1 | 0 | 11 | 1 | 1 | RW | 44751 | 4751 | 4750 | 0x03, 0x10 | Y | 0 |  | Refer Table 5
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44752 | 4752 | 4751 | 0x03, 0x10 | N | 0
AO1 Source Min Range | UINT16 | 2 | 1 | 0 | 1000 | 1 | 1 | RW | 44753 | 4753 | 4752 | 0x03, 0x10 | Y | 0 | Refer Table 5 | Refer Table 5
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44754 | 4754 | 4753 | 0x03, 0x10 | N | 0
AO1 Source Max Range | UINT16 | 2 | 1 | 0 | 1000 | 1 | 1 | RW | 44755 | 4755 | 4754 | 0x03, 0x10 | Y | 0 | Refer Table 5 | Refer Table 5
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44756 | 4756 | 4755 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44757 | 4757 | 4756 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44758 | 4758 | 4757 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44759 | 4759 | 4758 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44760 | 4760 | 4759 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44761 | 4761 | 4760 | 0x03, 0x10 | N | 0
AO2 Source | UINT16 | 2 | 1 | 0 | 11 | 1 | 1 | RW | 44762 | 4762 | 4761 | 0x03, 0x10 | Y | 0 |  | Refer Table 5
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44763 | 4763 | 4762 | 0x03, 0x10 | N | 0
AO2 Source Min Range | UINT16 | 2 | 1 | 0 | 1000 | 1 | 1 | RW | 44764 | 4764 | 4763 | 0x03, 0x10 | Y | 0 | Refer Table 5 | Refer Table 5
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44765 | 4765 | 4764 | 0x03, 0x10 | N | 0
AO2 Source Max Range | UINT16 | 2 | 1 | 0 | 1000 | 1 | 1 | RW | 44766 | 4766 | 4765 | 0x03, 0x10 | Y | 0 | Refer Table 5 | Refer Table 5
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44767 | 4767 | 4766 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44768 | 4768 | 4767 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44769 | 4769 | 4768 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44770 | 4770 | 4769 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44771 | 4771 | 4770 | 0x03, 0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44772 | 4772 | 4771 | 0x03, 0x10 | N | 0
Table 1
Mode |  | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
Local 1 |  | Custom Logic | Comm | Remote DI | Local DI | HMI
Local 2 |  | Custom Logic | Comm | Remote DI | Local DI | HMI
Local 3 |  | Custom Logic | Comm | Remote DI | Local DI | HMI
Remote |  | Custom Logic | Comm | Remote DI | Local DI | HMI
Condition
Table 2 | [6 empty] | Control buttons |  |  | single phase | Three phase
Starter Type |  | Value | Delay 1 | Delay 2 | Delay 3 | Delay 4 | Start | Stop
OVERLOAD |  | 0 | - | - | - | - | Start | Stop
DIRECT ONLINE |  | 1 | - | - | - | - | Forward Start | Reverse Start | Stop
REVERSIBLE DIRECT ONLINE |  | 2 | - | - | - | - |  |  | Stop
STAR DELTA |  | 3 | Time in Star | Change over Time | - | - |  |  | Stop
REVERSE STAR DELTA |  | 4 | Time in Star | Change over Time | - | - |  |  | Stop
DAHLANDER |  | 5 | - | Change over Time | - | -
REVERSE DAHLANDER |  | 6 | - | Change over Time | - | -
POLE CHANGING |  | 7 | - | Change over Time | - | -
REVERSE POLE CHANGING |  | 8 | - | Change over Time | - | -
CIRCUIT BREAKER CONTROL |  | 9 | - | - | - | -
SOFT STARTER CONTROL |  | 10 | - | - | Main Contactor Turn off Time | Capacitor Control Time
Custom Logic |  | 256-511
11
Table 3
DI Input Source |  | Value
Other |  | 0
Trip Reset DI |  | 1
Breaker Close DI |  | 2
Breaker Open DI |  | 3
Local-START> DI |  | 4
Local-START>> DI |  | 5
Local-STOP DI |  | 6
Local-START< DI |  | 7
Local-START<< DI |  | 8
Remote-START> DI |  | 9
Remote-START>> DI |  | 10
Remote-STOP DI |  | 11
Remote-START< DI |  | 12
Remote-START<< DI |  | 13
Interlock 1 |  | 14
Interlock 2 |  | 15
Interlock 3 |  | 16
Interlock 4 |  | 17
Interlock 5 |  | 18
Interlock 6 |  | 19
Interlock 7 |  | 20
Interlock 8 |  | 21
Interlock 9 |  | 22
Interlock 10 |  | 23
Interlock 11 |  | 24
Interlock 12 |  | 25
Contactor Open DI |  | 26
Run DI |  | 27
Block Input |  | 28
Logic Test DI |  | 29
Mode Selection 1 |  | 30
Mode Selection 2 |  | 31
Speed Change |  | 32
Forced start |  | 33
Forced stop |  | 34
Self Test without Trip |  | 35
Self Test with trip |  | 36
Soft Starter Reset DI |  | 37
NONE |  | 38
Table 4
DO Tag |  | Value
Other |  | 0
Device Internal DO |  | 1
Trip DO |  | 2
Alarm DO |  | 3
Pickup DO |  | 4
Inhibit DO |  | 5
Block OP |  | 6
CNTR OP 1 |  | 7
CNTR OP 2 |  | 8
CNTR OP 3 |  | 9
CNTR OP 4 |  | 10
CNTR OP 5 |  | 11
CNTR OP 6 |  | 12
Table 5
AO Source |  | Value | Min Value | Max Value | Multiplier | Unit
None |  | 0 | 0 | 0 | NA | NA
L1 RMS Current |  | 1 | 10 | 1000 | 1 | %FLC1
L2 RMS Current |  | 2 | 10 | 1000 | 1 | %FLC1
L3 RMS Current |  | 3 | 10 | 1000 | 1 | %FLC1
Average Current |  | 4 | 10 | 1000 | 1 | %FLC1
L1-L2 RMS Voltage / L1-N RMS Voltage |  | 5 | 20 | 150 | 1 | %Vn
L2-L3 RMS Voltage |  | 6 | 20 | 150 | 1 | %Vn
L3-L1 RMS Voltage |  | 7 | 20 | 150 | 1 | %Vn
Average Voltage |  | 8 | 20 | 150 | 1 | %Vn
System Frequency |  | 9 | 50 | 140 | 1 | %NominalHz
Total Active Power |  | 10 | 20 | 1000 | 1 | %Pn
Total Apparent Power |  | 11 | 20 | 1000 | 1 | %Pn
Table 6
DO settings | Overload | DOL | RDOL | STAR DELTA | R. STAR DELTA | DAHLANDER | R. DAHLANDER | Pole Changing | R. Pole changing | Circuit Breaker control | Soft Starter
DO1 Active Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO1 Input Source | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504
DO1 Tag | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
DO1 Output Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
DO1 Pulse Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0
DO2 Active Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO2 Input Source | 233 | 233 | 505 | 505 | 505 | 505 | 505 | 505 | 505 | 505 | 505
DO2 Tag | 3 | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
DO2 Output Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
DO2 Pulse Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0
DO3 Active Type | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO3 Input Source | 234 | 234 | 234 | 506 | 506 | 506 | 506 | 0 | 0 | 0 | 506
DO3 Tag | 2 | 2 | 2 | 9 | 9 | 9 | 9 | 0 | 0 | 0 | 9
DO3 Output Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO3 Pulse Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO4 Active Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO4 Input Source | 0 | 0 | 0 | 0 | 507 | 0 | 507 | 0 | 507 | 0 | 507
DO4 Tag | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 10
DO4 Output Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO4 Pulse Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO5 Active Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO5 Input Source | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 508 | 0 | 508
DO5 Tag | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | 0 | 11
DO5 Output Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DO5 Pulse Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table 7
DI settings | Overload | DOL | RDOL | STAR DELTA | R. STAR DELTA | DAHLANDER | R. DAHLANDER | Pole Changing | R. Pole changing | Circuit Breaker control | Soft Starter
DI1 Trigger Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI1 Input Source | 38 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
DI1 Validation Time | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DI2 Trigger Type | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
DI2 Input Source | 38 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
DI2 Validation Time | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DI3 Trigger Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI3 Input Source | 38 | 38 | 7 | 38 | 7 | 5 | 5 | 5 | 5 | 38 | 27
DI3 Validation Time | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DI4 Trigger Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI4 Input Source | 38 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
DI4 Validation Time | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DI5 Trigger Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI5 Input Source | 38 | 38 | 38 | 38 | 38 | 38 | 7 | 38 | 7 | 38 | 38
DI5 Validation Time | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DI6 Trigger Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DI6 Input Source | 38 | 38 | 38 | 38 | 38 | 38 | 8 | 38 | 8 | 38 | 38
DI6 Validation Time | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Note on B63: 0 - Disable 1 - HMI 2 - DI 3 - Communication
Note on B72: 0 - Momentary 1 - Permanent
Note on B73: 0 - Momentary 1 - Permanent
Note on B107: 0: Disable 1:Enable
Note on B116: 0: Disable 1: Enable
Note on B117: 0: No 1: Yes

## CompLogic Settings
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Truth Table Output value consideration:
NOTE |  | For Truth Table input index value refer "Lilliput - Comp_Logic_List" excel sheet | [14 empty] | This design can be explained with
2 Input 1 Output Truth Table settings | [16 empty] | the help of an example.
TT1 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45251 | 5251 | 5250 | 0x03,0x06,0x10 | Y | 0 |  |  | Consider the following truth table:
TT1 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45252 | 5252 | 5251 | 0x03,0x06,0x10 | Y | 0 |  |  | IP1 | IP2 | OP
TT1 Output Index | UINT16 | 2 | 1 | 0 | 15 | 1 | 1 | RW | 45253 | 5253 | 5252 | 0x03,0x06,0x10 | Y | 0 |  |  | 0 | 0 | 1 | (LSB)
TT2 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45254 | 5254 | 5253 | 0x03,0x06,0x10 | Y | 0 |  |  | 0 | 1 | 0
TT2 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45255 | 5255 | 5254 | 0x03,0x06,0x10 | Y | 0 |  |  | 1 | 0 | 1
TT2 Output Index | UINT16 | 2 | 1 | 0 | 15 | 1 | 1 | RW | 45256 | 5256 | 5255 | 0x03,0x06,0x10 | Y | 0 |  |  | 1 | 1 | 1 | (MSB)
3 Input 1 Output Truth Table settings | [16 empty] | The output will be in of four bits
TT1 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45257 | 5257 | 5256 | 0x03,0x06,0x10 | Y | 0 |  |  | having upper most bit i.e. of row 1 will be LSB.
TT1 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45258 | 5258 | 5257 | 0x03,0x06,0x10 | Y | 0 |  |  | Thus
TT1 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45259 | 5259 | 5258 | 0x03,0x06,0x10 | Y | 0 |  |  | Output = 1101
TT1 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45260 | 5260 | 5259 | 0x03,0x06,0x10 | Y | 0 |  |  | so in decimal=13
TT2 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45261 | 5261 | 5260 | 0x03,0x06,0x10 | Y | 0
TT2 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45262 | 5262 | 5261 | 0x03,0x06,0x10 | Y | 0
TT2 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45263 | 5263 | 5262 | 0x03,0x06,0x10 | Y | 0
TT2 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45264 | 5264 | 5263 | 0x03,0x06,0x10 | Y | 0
TT3 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45265 | 5265 | 5264 | 0x03,0x06,0x10 | Y | 0
TT3 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45266 | 5266 | 5265 | 0x03,0x06,0x10 | Y | 0
TT3 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45267 | 5267 | 5266 | 0x03,0x06,0x10 | Y | 0
TT3 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45268 | 5268 | 5267 | 0x03,0x06,0x10 | Y | 0
TT4 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45269 | 5269 | 5268 | 0x03,0x06,0x10 | Y | 0
TT4 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45270 | 5270 | 5269 | 0x03,0x06,0x10 | Y | 0
TT4 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45271 | 5271 | 5270 | 0x03,0x06,0x10 | Y | 0
TT4 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45272 | 5272 | 5271 | 0x03,0x06,0x10 | Y | 0
TT5 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45273 | 5273 | 5272 | 0x03,0x06,0x10 | Y | 0
TT5 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45274 | 5274 | 5273 | 0x03,0x06,0x10 | Y | 0
TT5 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45275 | 5275 | 5274 | 0x03,0x06,0x10 | Y | 0
TT5 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45276 | 5276 | 5275 | 0x03,0x06,0x10 | Y | 0
TT6 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45277 | 5277 | 5276 | 0x03,0x06,0x10 | Y | 0
TT6 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45278 | 5278 | 5277 | 0x03,0x06,0x10 | Y | 0
TT6 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45279 | 5279 | 5278 | 0x03,0x06,0x10 | Y | 0
TT6 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45280 | 5280 | 5279 | 0x03,0x06,0x10 | Y | 0
TT7 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45281 | 5281 | 5280 | 0x03,0x06,0x10 | Y | 0
TT7 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45282 | 5282 | 5281 | 0x03,0x06,0x10 | Y | 0
TT7 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45283 | 5283 | 5282 | 0x03,0x06,0x10 | Y | 0
TT7 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45284 | 5284 | 5283 | 0x03,0x06,0x10 | Y | 0
TT8 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45285 | 5285 | 5284 | 0x03,0x06,0x10 | Y | 0
TT8 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45286 | 5286 | 5285 | 0x03,0x06,0x10 | Y | 0
TT8 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45287 | 5287 | 5286 | 0x03,0x06,0x10 | Y | 0
TT8 Output Index | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45288 | 5288 | 5287 | 0x03,0x06,0x10 | Y | 0
5 Input 2 Output Truth Table settings
TT1 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45289 | 5289 | 5288 | 0x03,0x06,0x10 | Y | 0
TT1 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45290 | 5290 | 5289 | 0x03,0x06,0x10 | Y | 0
TT1 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45291 | 5291 | 5290 | 0x03,0x06,0x10 | Y | 0
TT1 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45292 | 5292 | 5291 | 0x03,0x06,0x10 | Y | 0
TT1 Input 5 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45293 | 5293 | 5292 | 0x03,0x06,0x10 | Y | 0
TT1 Output 1 Index | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 45294 | 5294 | 5293 | 0x03,0x06,0x10 | Y | 0
TT1 Output 2 Index | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 45296 | 5296 | 5295 | 0x03,0x06,0x10 | Y | 0
TT2 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45298 | 5298 | 5297 | 0x03,0x06,0x10 | Y | 0
TT2 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45299 | 5299 | 5298 | 0x03,0x06,0x10 | Y | 0
TT2 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45300 | 5300 | 5299 | 0x03,0x06,0x10 | Y | 0
TT2 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45301 | 5301 | 5300 | 0x03,0x06,0x10 | Y | 0
TT2 Input 5 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45302 | 5302 | 5301 | 0x03,0x06,0x10 | Y | 0
TT2 Output 1 Index | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 45303 | 5303 | 5302 | 0x03,0x06,0x10 | Y | 0
TT2 Output 2 Index | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 45305 | 5305 | 5304 | 0x03,0x06,0x10 | Y | 0
4 Input 1 Output Truth Table settings
TT1 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45307 | 5307 | 5306 | 0x03,0x06,0x10 | Y | 0
TT1 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45308 | 5308 | 5307 | 0x03,0x06,0x10 | Y | 0
TT1 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45309 | 5309 | 5308 | 0x03,0x06,0x10 | Y | 0
TT1 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45310 | 5310 | 5309 | 0x03,0x06,0x10 | Y | 0
TT1 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45311 | 5311 | 5310 | 0x03,0x06,0x10 | Y | 0
TT2 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45312 | 5312 | 5311 | 0x03,0x06,0x10 | Y | 0
TT2 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45313 | 5313 | 5312 | 0x03,0x06,0x10 | Y | 0
TT2 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45314 | 5314 | 5313 | 0x03,0x06,0x10 | Y | 0
TT2 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45315 | 5315 | 5314 | 0x03,0x06,0x10 | Y | 0
TT2 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45316 | 5316 | 5315 | 0x03,0x06,0x10 | Y | 0
TT3 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45317 | 5317 | 5316 | 0x03,0x06,0x10 | Y | 0
TT3 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45318 | 5318 | 5317 | 0x03,0x06,0x10 | Y | 0
TT3 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45319 | 5319 | 5318 | 0x03,0x06,0x10 | Y | 0
TT3 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45320 | 5320 | 5319 | 0x03,0x06,0x10 | Y | 0
TT3 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45321 | 5321 | 5320 | 0x03,0x06,0x10 | Y | 0
TT4 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45322 | 5322 | 5321 | 0x03,0x06,0x10 | Y | 0
TT4 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45323 | 5323 | 5322 | 0x03,0x06,0x10 | Y | 0
TT4 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45324 | 5324 | 5323 | 0x03,0x06,0x10 | Y | 0
TT4 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45325 | 5325 | 5324 | 0x03,0x06,0x10 | Y | 0
TT4 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45326 | 5326 | 5325 | 0x03,0x06,0x10 | Y | 0
TT5 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45327 | 5327 | 5326 | 0x03,0x06,0x10 | Y | 0
TT5 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45328 | 5328 | 5327 | 0x03,0x06,0x10 | Y | 0
TT5 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45329 | 5329 | 5328 | 0x03,0x06,0x10 | Y | 0
TT5 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45330 | 5330 | 5329 | 0x03,0x06,0x10 | Y | 0
TT5 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45331 | 5331 | 5330 | 0x03,0x06,0x10 | Y | 0
TT6 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45332 | 5332 | 5331 | 0x03,0x06,0x10 | Y | 0
TT6 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45333 | 5333 | 5332 | 0x03,0x06,0x10 | Y | 0
TT6 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45334 | 5334 | 5333 | 0x03,0x06,0x10 | Y | 0
TT6 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45335 | 5335 | 5334 | 0x03,0x06,0x10 | Y | 0
TT6 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45336 | 5336 | 5335 | 0x03,0x06,0x10 | Y | 0
TT7 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45337 | 5337 | 5336 | 0x03,0x06,0x10 | Y | 0
TT7 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45338 | 5338 | 5337 | 0x03,0x06,0x10 | Y | 0
TT7 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45339 | 5339 | 5338 | 0x03,0x06,0x10 | Y | 0
TT7 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45340 | 5340 | 5339 | 0x03,0x06,0x10 | Y | 0
TT7 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45341 | 5341 | 5340 | 0x03,0x06,0x10 | Y | 0
TT8 Input 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45342 | 5342 | 5341 | 0x03,0x06,0x10 | Y | 0
TT8 Input 2 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45343 | 5343 | 5342 | 0x03,0x06,0x10 | Y | 0
TT8 Input 3 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45344 | 5344 | 5343 | 0x03,0x06,0x10 | Y | 0
TT8 Input 4 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45345 | 5345 | 5344 | 0x03,0x06,0x10 | Y | 0
TT8 Output 1 Index | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45346 | 5346 | 5345 | 0x03,0x06,0x10 | Y | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45347 | 5347 | 5346 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45348 | 5348 | 5347 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45349 | 5349 | 5348 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45350 | 5350 | 5349 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45351 | 5351 | 5350 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45352 | 5352 | 5351 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45353 | 5353 | 5352 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45354 | 5354 | 5353 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45355 | 5355 | 5354 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45356 | 5356 | 5355 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45357 | 5357 | 5356 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45358 | 5358 | 5357 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45359 | 5359 | 5358 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45360 | 5360 | 5359 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45361 | 5361 | 5360 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45362 | 5362 | 5361 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45363 | 5363 | 5362 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45364 | 5364 | 5363 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45365 | 5365 | 5364 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45366 | 5366 | 5365 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45367 | 5367 | 5366 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45368 | 5368 | 5367 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45369 | 5369 | 5368 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45370 | 5370 | 5369 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45371 | 5371 | 5370 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45372 | 5372 | 5371 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45373 | 5373 | 5372 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45374 | 5374 | 5373 | 0x03,0x06,0x10 | N | 0
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45375 | 5375 | 5374 | 0x03,0x06,0x10 | N | 0
Timer Settings
Timer 1 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45376 | 5376 | 5375 | 0x03,0x06,0x10 | Y | 0
Timer 1 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | RW | 45377 | 5377 | 5376 | 0x03,0x06,0x10 | Y | 0
Timer 1 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45378 | 5378 | 5377 | 0x03,0x06,0x10 | Y | 0
Timer 1 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45379 | 5379 | 5378 | 0x03,0x06,0x10 | Y | 0
Timer 2 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45380 | 5380 | 5379 | 0x03,0x06,0x10 | Y | 0
Timer 2 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | RW | 45381 | 5381 | 5380 | 0x03,0x06,0x10 | Y | 0
Timer 2 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45382 | 5382 | 5381 | 0x03,0x06,0x10 | Y | 0
Timer 2 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45383 | 5383 | 5382 | 0x03,0x06,0x10 | Y | 0
Timer 3 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45384 | 5384 | 5383 | 0x03,0x06,0x10 | Y | 0
Timer 3 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | RW | 45385 | 5385 | 5384 | 0x03,0x06,0x10 | Y | 0
Timer 3 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45386 | 5386 | 5385 | 0x03,0x06,0x10 | Y | 0
Timer 3 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45387 | 5387 | 5386 | 0x03,0x06,0x10 | Y | 0
Timer 4 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45388 | 5388 | 5387 | 0x03,0x06,0x10 | Y | 0
Timer 4 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | RW | 45389 | 5389 | 5388 | 0x03,0x06,0x10 | Y | 0
Timer 4 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45390 | 5390 | 5389 | 0x03,0x06,0x10 | Y | 0
Timer 4 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45391 | 5391 | 5390 | 0x03,0x06,0x10 | Y | 0
SIGNAL CONDITIONER settings
Signal Conditioner 1 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45392 | 5392 | 5391 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 1 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45393 | 5393 | 5392 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 1 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45394 | 5394 | 5393 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 2 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45395 | 5395 | 5394 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 2 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45396 | 5396 | 5395 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 2 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45397 | 5397 | 5396 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 3 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45398 | 5398 | 5397 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 3 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45399 | 5399 | 5398 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 3 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45400 | 5400 | 5399 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 4 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45401 | 5401 | 5400 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 4 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45402 | 5402 | 5401 | 0x03,0x06,0x10 | Y | 0
Signal Conditioner 4 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45403 | 5403 | 5402 | 0x03,0x06,0x10 | Y | 0
NON VOLATILE settings
Non Volatile 1 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45404 | 5404 | 5403 | 0x03,0x06,0x10 | Y | 2
Non Volatile 1 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45405 | 5405 | 5404 | 0x03,0x06,0x10 | Y | 0
Non Volatile 1 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45406 | 5406 | 5405 | 0x03,0x06,0x10 | Y | 0
Non Volatile 2 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45407 | 5407 | 5406 | 0x03,0x06,0x10 | Y | 2
Non Volatile 2 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45408 | 5408 | 5407 | 0x03,0x06,0x10 | Y | 0
Non Volatile 2 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45409 | 5409 | 5408 | 0x03,0x06,0x10 | Y | 0
Non Volatile 3 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45410 | 5410 | 5409 | 0x03,0x06,0x10 | Y | 2
Non Volatile 3 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45411 | 5411 | 5410 | 0x03,0x06,0x10 | Y | 0
Non Volatile 3 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45412 | 5412 | 5411 | 0x03,0x06,0x10 | Y | 0
Non Volatile 4 Type | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45413 | 5413 | 5412 | 0x03,0x06,0x10 | Y | 2
Non Volatile 4 input | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45414 | 5414 | 5413 | 0x03,0x06,0x10 | Y | 0
Non Volatile 4 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45415 | 5415 | 5414 | 0x03,0x06,0x10 | Y | 0
COUNTER settings
Counter 1 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45416 | 5416 | 5415 | 0x03,0x06,0x10 | Y | 0
Counter 1 Input Up | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45417 | 5417 | 5416 | 0x03,0x06,0x10 | Y | 0
Counter 1 Input Down | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45418 | 5418 | 5417 | 0x03,0x06,0x10 | Y | 0
Counter 1 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45419 | 5419 | 5418 | 0x03,0x06,0x10 | Y | 0
Counter 2 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45420 | 5420 | 5419 | 0x03,0x06,0x10 | Y | 0
Counter 2 Input Up | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45421 | 5421 | 5420 | 0x03,0x06,0x10 | Y | 0
Counter 2 Input Down | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45422 | 5422 | 5421 | 0x03,0x06,0x10 | Y | 0
Counter 2 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45423 | 5423 | 5422 | 0x03,0x06,0x10 | Y | 0
Counter 3 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45424 | 5424 | 5423 | 0x03,0x06,0x10 | Y | 0
Counter 3 Input Up | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45425 | 5425 | 5424 | 0x03,0x06,0x10 | Y | 0
Counter 3 Input Down | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45426 | 5426 | 5425 | 0x03,0x06,0x10 | Y | 0
Counter 3 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45427 | 5427 | 5426 | 0x03,0x06,0x10 | Y | 0
Counter 4 Limit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45428 | 5428 | 5427 | 0x03,0x06,0x10 | Y | 0
Counter 4 Input Up | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45429 | 5429 | 5428 | 0x03,0x06,0x10 | Y | 0
Counter 4 Input Down | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45430 | 5430 | 5429 | 0x03,0x06,0x10 | Y | 0
Counter 4 Reset | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45431 | 5431 | 5430 | 0x03,0x06,0x10 | Y | 0
Programmable LED settings
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45432 | 5432 | 5431 | 0x03,0x06,0x10 | Y | 0 |  | On LED input
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45433 | 5433 | 5432 | 0x03,0x06,0x10 | Y | 0 |  | Flash LED input
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45434 | 5434 | 5433 | 0x03,0x06,0x10 | Y | 0 |  | Flicker LED input
Reserved
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45435 | 5435 | 5434 | 0x03,0x06,0x10 | Y | 0 |  | Comp logic input list
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45436 | 5436 | 5435 | 0x03,0x06,0x10 | Y | 0 |  | Comp logic input list
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45437 | 5437 | 5436 | 0x03,0x06,0x10 | Y | 0 |  | Comp logic input list
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45438 | 5438 | 5437 | 0x03,0x06,0x10 | Y | 0 |  | Comp logic input list
Reserved | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45439 | 5439 | 5438 | 0x03,0x06,0x10 | Y | 0 |  | Comp logic input list
Calculators
Calculator 1 - Input | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45440 | 5440 | 5439 | 0x03,0x06,0x10 | Y | 0
Calculator 1 - Numerator | INT16 | 2 | 1 | -32766 | 32767 | 1 | 1 | RW | 45441 | 5441 | 5440 | 0x03,0x06,0x10 | Y | 0
Calculator 1 - Denominator | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45442 | 5442 | 5441 | 0x03,0x06,0x10 | Y | 0
Calculator 1 - Offset | INT16 | 2 | 1 | -32766 | 32767 | 1 | 1 | RW | 45443 | 5443 | 5442 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Input 1 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45444 | 5444 | 5443 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Input 2 | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45445 | 5445 | 5444 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Numerator 1 | INT16 | 2 | 1 | -32766 | 32767 | 1 | 1 | RW | 45446 | 5446 | 5445 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Denominator 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45447 | 5447 | 5446 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Numerator 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45448 | 5448 | 5447 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Denominator 2 | INT16 | 2 | 1 | -32766 | 32767 | 1 | 1 | RW | 45449 | 5449 | 5448 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Offset_H | INT16 | 2 | 1 | -32766 | 32767 | 1 | 1 | RW | 45450 | 5450 | 5449 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Offset_L | INT16 | 2 | 1 | -32766 | 32767 | 1 | 1 | RW | 45451 | 5451 | 5450 | 0x03,0x06,0x10 | Y | 0
Calculator 2 - Operating Mode | UINT16 | 2 | 1 | 1 | 2 | 1 | 1 | RW | 45452 | 5452 | 5451 | 0x03,0x06,0x10 | Y | 1
Calculator 2 - Operator | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 45453 | 5453 | 5452 | 0x03,0x06,0x10 | Y | 0 |  | 0: Addition 1: Subtraction 2: Multiplication 3: Division
Analog Comparator Settings
Analog Comparator1 - AnalogInput | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45454 | 5454 | 5453 | 0x03,0x06,0x10 | Y | 0
Analog Comparator1 - LimitType | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45455 | 5455 | 5454 | 0x03,0x06,0x10 | Y | 0 |  | 0: Undershoot 1:Overshoot
Analog Comparator1 - TimeDelay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 45456 | 5456 | 5455 | 0x03,0x06,0x10 | Y | 0 | Seconds
Analog Comparator1 - MonitorLimit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45457 | 5457 | 5456 | 0x03,0x06,0x10 | Y | 0
Analog Comparator1 - ActivityStatus | UINT16 | 2 | 1 | 0 | 7 | 1 | 1 | RW | 45458 | 5458 | 5457 | 0x03,0x06,0x10 | Y | 0 |  | 1: Stop 2-: Start 3: Run
Analog Comparator1 - ResetLevel | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45459 | 5459 | 5458 | 0x03,0x06,0x10 | Y | 0
Analog Comparator2 - AnalogInput | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45460 | 5460 | 5459 | 0x03,0x06,0x10 | Y | 0
Analog Comparator2 - LimitType | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45461 | 5461 | 5460 | 0x03,0x06,0x10 | Y | 0 |  | 0: Undershoot 1:Overshoot
Analog Comparator2 - TimeDelay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 45462 | 5462 | 5461 | 0x03,0x06,0x10 | Y | 0 | Seconds
Analog Comparator2 - MonitorLimit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45463 | 5463 | 5462 | 0x03,0x06,0x10 | Y | 0
Analog Comparator2 - ActivityStatus | UINT16 | 2 | 1 | 0 | 7 | 1 | 1 | RW | 45464 | 5464 | 5463 | 0x03,0x06,0x10 | Y | 0 |  | 1: Stop 2-: Start 3: Run
Analog Comparator2 - ResetLevel | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45465 | 5465 | 5464 | 0x03,0x06,0x10 | Y | 0
Analog Comparator3 - AnalogInput | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45466 | 5466 | 5465 | 0x03,0x06,0x10 | Y | 0
Analog Comparator3 - LimitType | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45467 | 5467 | 5466 | 0x03,0x06,0x10 | Y | 0 |  | 0: Undershoot 1:Overshoot
Analog Comparator3 - TimeDelay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 45468 | 5468 | 5467 | 0x03,0x06,0x10 | Y | 0 | Seconds
Analog Comparator3 - MonitorLimit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45469 | 5469 | 5468 | 0x03,0x06,0x10 | Y | 0
Analog Comparator3 - ActivityStatus | UINT16 | 2 | 1 | 0 | 7 | 1 | 1 | RW | 45470 | 5470 | 5469 | 0x03,0x06,0x10 | Y | 0 |  | 1: Stop 2-: Start 3: Run
Analog Comparator3 - ResetLevel | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45471 | 5471 | 5470 | 0x03,0x06,0x10 | Y | 0
Analog Comparator4 - AnalogInput | UINT16 | 2 | 1 | 0 | 9249 | 1 | 1 | RW | 45472 | 5472 | 5471 | 0x03,0x06,0x10 | Y | 0
Analog Comparator4 - LimitType | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45473 | 5473 | 5472 | 0x03,0x06,0x10 | Y | 0 |  | 0: Undershoot 1:Overshoot
Analog Comparator4 - TimeDelay | UINT16 | 2 | 1 | 0 | 60000 | 1 | 1/10 | RW | 45474 | 5474 | 5473 | 0x03,0x06,0x10 | Y | 0 | Seconds
Analog Comparator4 - MonitorLimit | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45475 | 5475 | 5474 | 0x03,0x06,0x10 | Y | 0
Analog Comparator4 - ActivityStatus | UINT16 | 2 | 1 | 0 | 7 | 1 | 1 | RW | 45476 | 5476 | 5475 | 0x03,0x06,0x10 | Y | 0 |  | 1: Stop 2-: Start 3: Run
Analog Comparator4 - ResetLevel | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45477 | 5477 | 5476 | 0x03,0x06,0x10 | Y | 0
Note on B8: VRUND RANA: GATE VALUE AND 8 OR 14 XOR 6 NAND 7 NOR 1
Note on B11: VRUND RANA: VRUND RANA: GATE VALUE AND 8 OR 14 XOR 6 NAND 7 NOR 1
Note on B16: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B20: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B24: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B28: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B32: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B36: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B40: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B44: VRUND RANA: GATE VALUE AND 128 OR 254 XOR 150 NAND 127 NOR 1
Note on B51: VRUND RANA: GATE VALUE AND 2147483648 OR 4294967294 XOR 2523490710 NAND 2147483647 NOR 1
Note on B52: VRUND RANA: GATE VALUE AND 2147483648 OR 4294967294 XOR 2523490710 NAND 2147483647 NOR 1
Note on B58: VRUND RANA: GATE VALUE AND 2147483648 OR 4294967294 XOR 2523490710 NAND 2147483647 NOR 1
Note on B59: VRUND RANA: GATE VALUE AND 2147483648 OR 4294967294 XOR 2523490710 NAND 2147483647 NOR 1
Note on B65: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B70: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B75: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B80: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B85: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B90: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B95: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B100: VRUND RANA: GATE VALUE AND 32768 OR 65534 XOR 27030 NAND 32767 NOR 1
Note on B131: VRUND RANA: /* Timer types */ WITH_CLOSING_DELAY 0 CLOSING_DELAY_WITH_MEMORY 1 WITH_OPENING_DELAY 2 WITH_FLEETING_CLOSING 3
Note on B135: VRUND RANA: /* Timer types */ WITH_CLOSING_DELAY 0 CLOSING_DELAY_WITH_MEMORY 1 WITH_OPENING_DELAY 2 WITH_FLEETING_CLOSING 3
Note on B139: VRUND RANA: /* Timer types */ WITH_CLOSING_DELAY 0 CLOSING_DELAY_WITH_MEMORY 1 WITH_OPENING_DELAY 2 WITH_FLEETING_CLOSING 3
Note on B143: VRUND RANA: /* Timer types */ WITH_CLOSING_DELAY 0 CLOSING_DELAY_WITH_MEMORY 1 WITH_OPENING_DELAY 2 WITH_FLEETING_CLOSING 3
Note on B148: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B151: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B154: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B157: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B161: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B164: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B167: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3
Note on B170: VRUND RANA: /* Signal Conditioner Types */ NON_INVERTING 0 INVERTING 1 EDGE_RISING_WITH_MEMORY 2 EDGE_FALING_WITH_MEMORY 3

## DO_CompLogic_List
DO Input source / COMP LOGIC INPUT LIST
Index | Signal Name | Description | Remarks
0 | None
1 | Fixed 0
2 | Fixed 1
3 | Reserved
4 | Reserved
5 | Reserved
6 | Reserved
7 | RESET_KEY(Main unit)
8 | DI 1
9 | DI 2
10 | DI 3
11 | DI 4
12 | DI 5
13 | DI 6
14 | DI 7
15 | DI 8
16 | DI 9
17 | DI 10
18 | DI 11
19 | DI 12
20 | DI 13
21 | DI 14
22 | DI 15
23 | DI 16
24 | DI 17
25 | DI 18
26 | DI 19
27 | DI 20
28 | DI 21
29 | DI 22
30 | DI 23
31 | DI 24
32 | DI 25
33 | DI 26
34 | DI 27
35 | DI 28
36 | DI 29
37 | DI 30
38 | DI 31
39 | DI 32
40 | DO 1
41 | DO 2
42 | DO 3
43 | DO 4
44 | DO 5
45 | DO 6
46 | DO 7
47 | DO 8
48 | DO 9
49 | DO 10
50 | DO 11
51 | DO 12
52 | DO 13
53 | Reserved
54 | Reserved
55 | Reserved
56 | Reserved
57 | Reserved
58 | Reserved
59 | Reserved
60 | Reserved
61 | Reserved
62 | Reserved
63 | Reserved
64 | Reserved
65 | Reserved
66 | Reserved
67 | Reserved
68 | Reserved
69 | Reserved
70 | Reserved
71 | Reserved
72 | Reserved
73 | Reserved
74 | Reserved
75 | Reserved
76 | Reserved
77 | Reserved
78 | Reserved
79 | Reserved
80 | Reserved
81 | Reserved
82 | Reserved
83 | Reserved
84 | Reserved
85 | Reserved
86 | Reserved
87 | Reserved
88 | Reserved
89 | Reserved
90 | Reserved
91 | Reserved
92 | Reserved
93 | Reserved
94 | Reserved
95 | Reserved
96 | Reserved
97 | Reserved
98 | Reserved
99 | Reserved
100 | Reserved
101 | Reserved
102 | Reserved
103 | Reserved
104 | 2IP_1OP_TT1
105 | 2IP_1OP_TT2
106 | Reserved
107 | Reserved
108 | Reserved
109 | Reserved
110 | Reserved
111 | Reserved
112 | 3IP_1OP_TT1
113 | 3IP_1OP_TT2
114 | 3IP_1OP_TT3
115 | 3IP_1OP_TT4
116 | 3IP_1OP_TT5
117 | 3IP_1OP_TT6
118 | 3IP_1OP_TT7
119 | 3IP_1OP_TT8
120 | 5IP_2OP_TT1_OP1
121 | 5IP_2OP_TT1_OP2
122 | 5IP_2OP_TT2_OP1
123 | 5IP_2OP_TT2_OP2
124 | Reserved
125 | Reserved
126 | Reserved
127 | Reserved
128 | 4IP_1OP_TT1
129 | 4IP_1OP_TT2
130 | 4IP_1OP_TT3
131 | 4IP_1OP_TT4
132 | 4IP_1OP_TT5
133 | 4IP_1OP_TT6
134 | 4IP_1OP_TT7
135 | 4IP_1OP_TT8
136 | Timer OP 1
137 | Timer OP 2
138 | Timer OP 3
139 | Timer OP 4
140 | Reserved
141 | Reserved
142 | Reserved
143 | Reserved
144 | Reserved
145 | Reserved
146 | Reserved
147 | Reserved
148 | Reserved
149 | Reserved
150 | Reserved
151 | Reserved
152 | Counter OP 1
153 | Counter OP 2
154 | Counter OP 3
155 | Counter OP 4
156 | Reserved
157 | Reserved
158 | Reserved
159 | Reserved
160 | Reserved
161 | Reserved
162 | Reserved
163 | Reserved
164 | Reserved
165 | Reserved
166 | Reserved
167 | Reserved
168 | Signal Conditioner OP 1
169 | Signal Conditioner OP 2
170 | Signal Conditioner OP 3
171 | Signal Conditioner OP 4
172 | Reserved
173 | Reserved
174 | Reserved
175 | Reserved
176 | Reserved
177 | Reserved
178 | Reserved
179 | Reserved
180 | Reserved
181 | Reserved
182 | Reserved
183 | Reserved
184 | Non Volatile Element OP 1
185 | Non Volatile Element OP 2
186 | Non Volatile Element OP 3
187 | Non Volatile Element OP 4
188 | Reserved
189 | Reserved
190 | Reserved
191 | Reserved
192 | Reserved
193 | Reserved
194 | Reserved
195 | Reserved
196 | Reserved
197 | Reserved
198 | Reserved
199 | Reserved
200 | Analog Comparator OP 1
201 | Analog Comparator OP 2
202 | Analog Comparator OP 3
203 | Analog Comparator OP 4
204 | Reserved
205 | Reserved
206 | Reserved
207 | Reserved
208 | Reserved
209 | Reserved
210 | Reserved
211 | Reserved
212 | Reserved
213 | Reserved
214 | Reserved
215 | Reserved
216 | Reserved
217 | Reserved
218 | Reserved
219 | Reserved
220 | Reserved
221 | Reserved
222 | Reserved
223 | Reserved
224 | Reserved
225 | Reserved
226 | Reserved
227 | Reserved
228 | Reserved
229 | Reserved
230 | Reserved
231 | Reserved
232 | Pickup status
233 | alarm status
234 | Trip Status
235 | Motor stop error detection
236 | Reserved
237 | Block Output
238 | Reserved
239 | Reserved
240 | Reserved
241 | Reserved
242 | Reserved
243 | Reserved
244 | Reserved
245 | Reserved
246 | Reserved
247 | Reserved
248 | Motor Stop
249 | Motor Start
250 | Motor Run
251 | Motor Inhibit
252 | Reserved
253 | Reserved
254 | Reserved
255 | Reserved
256 | Reserved
257 | Reserved
258 | Reserved
259 | Reserved
260 | Reserved
261 | Reserved
262 | Reserved
263 | Reserved
264 | Thermal Overload Alarm
265 | Locked Rotor Alarm
266 | Stalled Rotor Alarm
267 | Definite time overcurrent Alarm
268 | Normal inverse overcurrent Alarm
269 | Short time overcurrent Alarm
270 | Calculated ground current Alarm
271 | Measured ground current Alarm
272 | Under Current Alarm
273 | Current Imbalance Alarm
274 | Current Phase Loss Alarm
275 | Current Phase Reversal Alarm
276 | Under Voltage Alarm
277 | Over Voltage Alarm
278 | Voltage Phase Loss Alarm
279 | Voltage Imbalance Alarm
280 | Voltage Phase Reversal Alarm
281 | Under Frequency Alarm
282 | Over Frequency Alarm
283 | Reserved
284 | Communication loss Alarm
285 | Over Temperature Alarm
286 | Under Power Alarm
287 | Over Power Alarm
288 | Under Power factor Alarm
289 | Reserved
290 | Reserved
291 | HMI communication loss Alarm
292 | Reserved
293 | Reserved
294 | Reserved
295 | Reserved
296 | Thermal Overload Pickup
297 | Locked Rotor Pickup
298 | Stalled Rotor Pickup
299 | Definite time overcurrent Pickup
300 | Normal inverse overcurrent Pickup
301 | Short time overcurrent Pickup
302 | Calculated ground current Pickup
303 | Measured ground current Pickup
304 | Under Current Pickup
305 | Current Imbalance Pickup
306 | Current Phase Loss Pickup
307 | Current Phase Reversal Pickup
308 | Under Voltage Pickup
309 | Over Voltage Pickup
310 | Voltage Phase Loss Pickup
311 | Voltage Imbalance Pickup
312 | Voltage Phase Reversal Pickup
313 | Under Frequency Pickup
314 | Over Frequency Pickup
315 | Reserved |  | Excessive start time Pickup
316 | Communication loss Pickup
317 | Over Temperature Pickup
318 | Under Power Pickup
319 | Over Power Pickup
320 | Under Power factor Pickup
321 | Reserved
322 | Reserved
323 | HMI communication loss Pickup
324 | Reserved
325 | Reserved
326 | Reserved
327 | Reserved
328 | Thermal Overload Trip
329 | Locked Rotor Trip
330 | Stalled Rotor Trip
331 | Definite time overcurrent Trip
332 | Normal inverse overcurrent Trip
333 | Short time overcurrent Trip
334 | Calculated ground current Trip
335 | Measured ground current Trip
336 | Under Current Trip
337 | Current Imbalance Trip
338 | Current Phase Loss Trip
339 | Current Phase Reversal Trip
340 | Under Voltage Trip
341 | Over Voltage Trip
342 | Voltage Phase Loss Trip
343 | Voltage Imbalance Trip
344 | Voltage Phase Reversal Trip
345 | Under Frequency Trip
346 | Over Frequency Trip
347 | Reserved |  | Excessive start time trip
348 | Communication loss Trip
349 | Over Temperature Trip
350 | Under Power Trip
351 | Over Power Trip
352 | Under Power factor Trip
353 | Reserved
354 | Reserved
355 | HMI communication loss Trip
356 | Reserved
357 | Reserved
358 | Reserved
359 | Reserved
360 | Interlock 1 Alarm
361 | Interlock 2 Alarm
362 | Interlock 3 Alarm
363 | Interlock 4 Alarm
364 | Interlock 5 Alarm
365 | Interlock 6 Alarm
366 | Interlock 7 Alarm
367 | Interlock 8 Alarm
368 | Interlock 9 Alarm
369 | Interlock 10 Alarm
370 | Interlock 11 Alarm
371 | Interlock 12 Alarm
372 | Reserved
373 | Reserved
374 | Reserved
375 | Reserved
376 | Interlock 1 Pickup
377 | Interlock 2 Pickup
378 | Interlock 3 Pickup
379 | Interlock 4 Pickup
380 | Interlock 5 Pickup
381 | Interlock 6 Pickup
382 | Interlock 7 Pickup
383 | Interlock 8 Pickup
384 | Interlock 9 Pickup
385 | Interlock 10 Pickup
386 | Interlock 11 Pickup
387 | Interlock 12 Pickup
388 | Reserved
389 | Reserved
390 | Reserved
391 | Reserved
392 | Interlock 1 Trip
393 | Interlock 2 Trip
394 | Interlock 3 Trip
395 | Interlock 4 Trip
396 | Interlock 5 Trip
397 | Interlock 6 Trip
398 | Interlock 7 Trip
399 | Interlock 8 Trip
400 | Interlock 9 Trip
401 | Interlock 10 Trip
402 | Interlock 11 Trip
403 | Interlock 12 Trip
404 | Reserved
405 | Reserved
406 | Reserved
407 | Reserved
408 | AI1 Alarm
409 | AI2 Alarm
410 | AI3 Alarm
411 | AI4 Alarm
412 | Reserved
413 | Reserved
414 | Reserved
415 | Reserved
416 | Reserved
417 | Reserved
418 | Reserved
419 | Reserved
420 | Reserved
421 | Reserved
422 | Reserved
423 | Reserved
424 | AI1 Pickup
425 | AI2 Pickup
426 | AI3 Pickup
427 | AI4 Pickup
428 | Reserved
429 | Reserved
430 | Reserved
431 | Reserved
432 | Reserved
433 | Reserved
434 | Reserved
435 | Reserved
436 | Reserved
437 | Reserved
438 | Reserved
439 | Reserved
440 | AI1 Trip
441 | AI2 Trip
442 | AI3 Trip
443 | AI4 Trip
444 | Reserved
445 | Reserved
446 | Reserved
447 | Reserved
448 | Reserved
449 | Reserved
450 | Reserved
451 | Reserved
452 | Reserved
453 | Reserved
454 | Reserved
455 | Reserved
456 | TI1 Alarm
457 | TI2 Alarm
458 | TI3 Alarm
459 | TI4 Alarm
460 | TI5 Alarm
461 | TI6 Alarm
462 | TI7 Alarm
463 | TI8 Alarm
464 | TI9 Alarm
465 | TI10 Alarm
466 | TI11 Alarm
467 | TI12 Alarm
468 | TI13 Alarm
469 | TI14 Alarm
470 | TI15 Alarm
471 | Reserved
472 | TI1 Pickup
473 | TI2 Pickup
474 | TI3 Pickup
475 | TI4 Pickup
476 | TI5 Pickup
477 | TI6 Pickup
478 | TI7 Pickup
479 | TI8 Pickup
480 | TI9 Pickup
481 | TI10 Pickup
482 | TI11 Pickup
483 | TI12 Pickup
484 | TI13 Pickup
485 | TI14 Pickup
486 | TI15 Pickup
487 | Reserved
488 | TI1 Trip
489 | TI2 Trip
490 | TI3 Trip
491 | TI4 Trip
492 | TI5 Trip
493 | TI6 Trip
494 | TI7 Trip
495 | TI8 Trip
496 | TI9 Trip
497 | TI10 Trip
498 | TI11 Trip
499 | TI12 Trip
500 | TI13 Trip
501 | TI14 Trip
502 | TI15 Trip
503 | Reserved
504 | CONTACTOR OUTPUT 1
505 | CONTACTOR OUTPUT 2
506 | CONTACTOR OUTPUT 3
507 | CONTACTOR OUTPUT 4
508 | CONTACTOR OUTPUT 5
509 | Reserved
510 | Reserved
511 | Reserved
512 | Reserved
513 | Reserved
514 | Reserved
515 | Reserved
516 | Reserved
517 | Reserved
518 | Reserved
519 | Reserved
520 | Reserved
521 | Reserved
522 | Reserved
523 | Reserved
524 | Reserved
525 | Reserved
526 | Reserved
527 | Reserved
528 | Reserved
529 | Reserved
530 | Reserved
531 | Reserved
532 | Reserved
533 | Reserved
534 | Reserved
535 | Motor forward running
536 | Motor reverse running
537 | Motor fast forward running
538 | Motor fast reverse running
539 | Motor running in star (Forward)
540 | Motor running in delta (Forward)
541 | Motor running in star (Reverse)
542 | Motor running in delta (Reverse)
543 | Motor in star-delta changeover (forward)
544 | Motor in star-delta changeover (reverse)
545 | Interlocking time active
546 | Change-over pause active
547 | Reserved
548 | Reserved
549 | Reserved
550 | Reserved
551 | Reserved
552 | Status - Permissive Command 1
553 | Status - Permissive Command 2
554 | Status - Permissive Command 3
555 | Status - Permissive Command 4
556 | Status - Permissive Command 5
557 | Status - Permissive Command 6
558 | Status - Permissive Command 7
559 | Status - Permissive Command 8
560 | Reserved
561 | Reserved
562 | Reserved
563 | Reserved
564 | Reserved
565 | Reserved
566 | Reserved
567 | Reserved
568 | Reserved
569 | Reserved
570 | Reserved
571 | Reserved
572 | Reserved
573 | Reserved
574 | Reserved
575 | Reserved
576 | Reserved
577 | Reserved
578 | Reserved
579 | Reserved
580 | Reserved
581 | Reserved
582 | Reserved
583 | Reserved
584 | No Voltage Inhibit
585 | Under Voltage Inhibit
586 | Trip Inhibit
587 | Thermal Inhibit
588 | Max Starts Inhibit
589 | Interlock 1 Inhibit
590 | Interlock 2 Inhibit
591 | Interlock 3 Inhibit
592 | Interlock 4 Inhibit
593 | Interlock 5 Inhibit
594 | Interlock 6 Inhibit
595 | Interlock 7 Inhibit
596 | Interlock 8 Inhibit
597 | Interlock 9 Inhibit
598 | Interlock 10 Inhibit
599 | Interlock 11 Inhibit
600 | Interlock 12 Inhibit
601 | Local DI Stop Inhibit
602 | Remote DI Stop Inhibit
603 | Communication Stop Inhibit
604 | Force Stop Inhibit
605 | Antibackspin Inhibit
606 | Reserved
607 | Direction change Inhibit
608 | Speed change Inhibit
609 | Custom Stop Inhibit
610 | Reserved
611 | Reserved
612 | Reserved
613 | Reserved
614 | Reserved
615 | Reserved
616 | Sensor module communication error detected
617 | Expansion module communication error detected
618 | Reserved |  | HMI Communication error detected
619 | EEPROM interface error detected
620 | EEPROM checksum error detected
621 | Configuration error detected
622 | Reserved
623 | reserved
624 | Watchdog timeout detected
625 | reserved
626 | Reserved
627 | Reserved
628 | Energy Register Overflow
629 | Error detected during expansion module initialization
630 | reserved
631 | Reserved
632 | Reserved
633 | Reserved
634 | Reserved
635 | Reserved
636 | Reserved
637 | Reserved
638 | Reserved
639 | Reserved
640 | Reserved
641 | Reserved
642 | Reserved
643 | Reserved
644 | Reserved
645 | Reserved
646 | Reserved
647 | Reserved
648 | SM Watchdog timeout detected
649 | ADC conversion error detected
650 | Flash error detected
651 | Reserved
652 | Voltage configuration not detected
653 | Reserved
654 | Calibration error detected
655 | VL1 measurement error detected
656 | VL2 measurement error detected
657 | VL3 measurement error detected
658 | IL1 low gain measurement error detected
659 | IL1 high gain measurement error detected
660 | IL2 low gain measurement error detected
661 | IL2 high gain measurement error detected
662 | IL3 low gain measurement error detected
663 | IL3 high gain measurement error detected
664 | Reserved
665 | Reserved
666 | Reserved
667 | Reserved
668 | Reserved
669 | Reserved
670 | Reserved
671 | Reserved
672 | Reserved
673 | Reserved
674 | Reserved
675 | Reserved
676 | Reserved
677 | Reserved
678 | Reserved
679 | Reserved
680 | Reserved
681 | Reserved
682 | Reserved
683 | Reserved
684 | Reserved
685 | Reserved
686 | Reserved
687 | Reserved
688 | Reserved
689 | Reserved
690 | Reserved
691 | Reserved
692 | Reserved
693 | Reserved
694 | Reserved
695 | Reserved
696 | Reserved
697 | Reserved
698 | Reserved
699 | Reserved
700 | Reserved
701 | Reserved
702 | Reserved
703 | Reserved
704 | Reserved
705 | Reserved
706 | Reserved
707 | Reserved
708 | Reserved
709 | Reserved
710 | Reserved
711 | Reserved
712-65534 | Reserved
65535 | Custom Logic |  | This Index is not applicable in Comp Logic, Only Applicable for DO input source

## Monitoring Data
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks | EIP Address
Metering Data | [16 empty] | 72:01 | Hex |  | address | file name | word size | Min_Value | MaxL_Value | MaxH_Value | step_size
L1 RMS current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45501 | 5501 | 5500 | 0x03 | N | A |  |  | 1 | 1 |  | 15501 | 0x0120 | 2 | 0 | 50000000 | 0 | 1
L2 RMS current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45503 | 5503 | 5502 | 0x03 | N | A |  |  | 2 | 2 |  | 15503 | 0x0120 | 2 | 0 | 50000000 | 0 | 1
L3 RMS current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45505 | 5505 | 5504 | 0x03 | N | A |  |  | 3 | 3 |  | 15505 | 0x0120 | 2 | 0 | 50000000 | 0 | 1
Measured ground current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45507 | 5507 | 5506 | 0x03 | N | A |  |  | 4 | 4 |  | 15507 | 0x0120 | 2 | 0 | 50000000 | 0 | 1
Calculated ground current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45509 | 5509 | 5508 | 0x03 | N | A |  |  | 5 | 5 |  | 15509 | 0x0120 | 2 | 0 | 50000000 | 0 | 1
Average Current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45511 | 5511 | 5510 | 0x03 | N | A |  |  | 6 | 6 |  | 15511 | 0x0120 | 2 | 0 | 50000000 | 0 | 1
Current Imbalance | UINT16 | 2 | 1 | 0 | 10000 | 1 | 1/100 | R | 45513 | 5513 | 5512 | 0x03 | N | % |  |  | 7 | 7 |  | 15513 | 0x0120 | 1 | 0 | 10000 | 0 | 1
Current Phase sequence | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | R | 45514 | 5514 | 5513 | 0x03 | N | - |  | 0: - 1: L123 2: L132 3: CTWF (CT wiring fault) | 8 | 8 |  | 15514 | 0x0120 | 1 | 0 | 3 | 0 | 1
L1-L2 RMS voltage / L1-N RMS voltage | UINT32 | 4 | 2 | 0 | 14300 | 1 | 1/10 | R | 45515 | 5515 | 5514 | 0x03 | N | V |  |  | 9 | 9 |  | 15515 | 0x0120 | 2 | 0 | 14300 | 0 | 1
L2-L3 RMS voltage | UINT32 | 4 | 2 | 0 | 14300 | 1 | 1/10 | R | 45517 | 5517 | 5516 | 0x03 | N | V |  |  | 10 | A |  | 15517 | 0x0120 | 2 | 0 | 14300 | 0 | 1
L3-L1 RMS voltage | UINT32 | 4 | 2 | 0 | 14300 | 1 | 1/10 | R | 45519 | 5519 | 5518 | 0x03 | N | V |  |  | 11 | B |  | 15519 | 0x0120 | 2 | 0 | 14300 | 0 | 1
Average Voltage | UINT32 | 4 | 2 | 0 | 14300 | 1 | 1/10 | R | 45521 | 5521 | 5520 | 0x03 | N | V |  |  | 12 | C |  | 15521 | 0x0120 | 2 | 0 | 14300 | 0 | 1
Voltage Imbalance | UINT16 | 2 | 1 | 0 | 10000 | 1 | 1/100 | R | 45523 | 5523 | 5522 | 0x03 | N | % |  |  | 13 | D |  | 15523 | 0x0120 | 1 | 0 | 10000 | 0 | 1
Voltage Phase sequence | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | R | 45524 | 5524 | 5523 | 0x03 | N | - |  | 0: - 1: L123 2: L132 | 14 | E |  | 15524 | 0x0120 | 1 | 0 | 2 | 0 | 1
System Frequency | UINT16 | 2 | 1 | 0 | 7000 | 1 | 1/100 | R | 45525 | 5525 | 5524 | 0x03 | N | Hz |  |  | 15 | F |  | 15525 | 0x0120 | 1 | 0 | 7000 | 0 | 1
System PF | UINT16 | 2 | 1 | 0 | 100 | 1 | 1/100 | R | 45526 | 5526 | 5525 | 0x03 | N | - |  |  | 16 | 10 |  | 15526 | 0x0120 | 1 | 0 | 100 | 0 | 1
Total Active Power | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/1000 | R | 45527 | 5527 | 5526 | 0x03 | N | KW |  |  | 17 | 11 |  | 15527 | 0x0120 | 2 | 0 | 4294967295 | 0 | 1
Total Reactive Power | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/1000 | R | 45529 | 5529 | 5528 | 0x03 | N | KVAR |  |  | 18 | 12 |  | 15529 | 0x0120 | 2 | 0 | 4294967295 | 0 | 1
Total Apparent Power | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/1000 | R | 45531 | 5531 | 5530 | 0x03 | N | KVA |  |  | 19 | 13 |  | 15531 | 0x0120 | 2 | 0 | 4294967295 | 0 | 1
Total Active Energy | UINT64 | 8 | 4 | 0 | 9.2234e+18 | 1 | 1/1000 | R | 45533 | 5533 | 5532 | 0x03 | Y | KWh |  |  | 20 | 14 |  | 15533 | 0x0120 | 4 | 0 | 9.2234e+18 | 0 | 1
Total Reactive Energy | UINT64 | 8 | 4 | 0 | 9.2234e+18 | 1 | 1/1000 | R | 45537 | 5537 | 5536 | 0x03 | Y | KVARh |  |  | 21 | 15 |  | 15537 | 0x0120 | 4 | 0 | 9.2234e+18 | 0 | 1
Total Apparent Energy | UINT64 | 8 | 4 | 0 | 9.2234e+18 | 1 | 1/1000 | R | 45541 | 5541 | 5540 | 0x03 | Y | KVah |  |  | 22 | 16 |  | 15541 | 0x0120 | 4 | 0 | 9.2234e+18 | 0 | 1
L1 Current THD | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45545 | 5545 | 5544 | 0x03 | N | % |  |  | 23 | 17 |  | 15545 | 0x0120 | 1 | 0 | 100 | 0 | 1
L2 Current THD | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45546 | 5546 | 5545 | 0x03 | N | % |  |  | 24 | 18 |  | 15546 | 0x0120 | 1 | 0 | 100 | 0 | 1
L3 Current THD | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45547 | 5547 | 5546 | 0x03 | N | % |  |  | 25 | 19 |  | 15547 | 0x0120 | 1 | 0 | 100 | 0 | 1
L1-L2 Voltage THD / L1-N Voltage THD | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45548 | 5548 | 5547 | 0x03 | N | % |  |  | 26 | 1A |  | 15548 | 0x0120 | 1 | 0 | 100 | 0 | 1
L2-L3 Voltage THD | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45549 | 5549 | 5548 | 0x03 | N | % |  |  | 27 | 1B
L3-L1 Voltage THD | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45550 | 5550 | 5549 | 0x03 | N | % |  |  | 28 | 1C
PT100 | UINT16 | 2 | 1 | 0 | 3000 | 1 | 1/10 | R | 45551 | 5551 | 5550 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement | 29 | 1D |  | 15551 | 0x0120 | 1 | 0 | 3000 | 0 | 1
PTC Temperature in Ohm | UINT16 | 2 | 1 | 0 | 4000 | 1 | 1 | R | 45552 | 5552 | 5551 | 0x03 | N | Ohm |  |  | 30 | 1E |  | 15552 | 0x0120 | 1 | 0 | 4000 | 0 | 1
Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45553 | 5553 | 5552 | 0x03 | N |  |  |  | 31 | 1F |  | 15553 | 0x0120 | 1 | 0 | 0 | 0 | 1
Reserved | UINT32 | 4 | 2 | 0 | 0 | 1 | 1 | R | 45554 | 5554 | 5553 | 0x03 | N |  |  |  | 32 | 20 |  | 15554 | 0x0120 | 2 | 0 | 0 | 0 | 1
Reserved | UINT32 | 4 | 2 | 0 | 0 | 1 | 1 | R | 45556 | 5556 | 5555 | 0x03 | N |  |  |  | 33 | 21 |  | 15556 | 0x0120 | 2 | 0 | 0 | 0 | 1
need | [16 empty] | 72:02 | HEX
MotorStatus | UINT16 | 2 | 1 | 1 | 4 | 1 | 1 | R | 45558 | 5558 | 5557 | 0x03 | N |  |  | 1- Stop 2- Start 4- Run | 1 | 1
Thermal Memory | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | R | 45559 | 5559 | 5558 | 0x03 | Y | % |  |  | 2 | 2
Thermal Time to trip | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45560 | 5560 | 5559 | 0x03 | N | seconds |  |  | 3 | 3
Thermal Time to cool | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45562 | 5562 | 5561 | 0x03 | N | seconds |  |  | 4 | 4
Max starts counter | UINT16 | 2 | 1 | 0 | 30 | 1 | 1 | R | 45564 | 5564 | 5563 | 0x03 | Y |  |  |  | 5 | 5
Max start inhibit time | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45565 | 5565 | 5564 | 0x03 | Y | seconds |  |  | 6 | 6
Motor Starting peak current | UINT32 | 4 | 2 | 0 | 50000000 | 1 | 1/1000 | R | 45567 | 5567 | 5566 | 0x03 | N | A |  |  | 7 | 7
Motor Starting time | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1/1000 | R | 45569 | 5569 | 5568 | 0x03 | N | seconds |  |  | 8 | 8
Total run hour | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45571 | 5571 | 5570 | 0x03 | Y | Minute |  |  | 9 | 9
Last run hour | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45573 | 5573 | 5572 | 0x03 | Y | Minute |  |  | 10 | A
Number of Starts | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45575 | 5575 | 5574 | 0x03 | Y |  |  |  | 11 | B
Number of Stops | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45576 | 5576 | 5575 | 0x03 | Y |  |  |  | 12 | C
Motor Stop Cause | UINT16 | 2 | 1 | 0 | 15 | 1 | 1 | R | 45577 | 5577 | 5576 | 0x03 | Y |  |  | 0: None 1: HMI / DTM 2: LOCAL DI 3: REMOTE DI 4: Communication 5: Voltage Dip 6: Trip 7: No Current 8: Forced Stop 9: Change Direction 10: No Feedback 11: Change Speed 12: Custom Command 13: Mode Transfer 14: Reserved (Fallback mode will be implemented in Wave 2 of Ethernet) 15: No Voltage | 13 | D
Trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45578 | 5578 | 5577 | 0x03 | Y |  |  |  | 14 | E
Last Motor Start Time Stamp
Day | UINT16 | 2 | 1 | 1 | 31 | 1 | 1 | R | 45579 | 5579 | 5578 | 0x03 | Y
Month | UINT16 | 2 | 1 | 1 | 12 | 1 | 1 | R | 45580 | 5580 | 5579 | 0x03 | Y
Year | UINT16 | 2 | 1 | 2010 | 2999 | 1 | 1 | R | 45581 | 5581 | 5580 | 0x03 | Y
Hour | UINT16 | 2 | 1 | 0 | 23 | 1 | 1 | R | 45582 | 5582 | 5581 | 0x03 | Y | Hour
Minute | UINT16 | 2 | 1 | 0 | 59 | 1 | 1 | R | 45583 | 5583 | 5582 | 0x03 | Y | Minute
Second | UINT16 | 2 | 1 | 0 | 59 | 1 | 1 | R | 45584 | 5584 | 5583 | 0x03 | Y | Second
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | R | 45585 | 5585 | 5584 | 0x03 | N
Analog Module Data
Analog input 1 | INT16 | 2 | 1 | -200 | 200 | 1 | 1/10 | R | 45586 | 5586 | 5585 | 0x03 | N | mA
Analog input 2 | INT16 | 2 | 1 | -200 | 200 | 1 | 1/10 | R | 45587 | 5587 | 5586 | 0x03 | N | mA
Analog input 3 | INT16 | 2 | 1 | -200 | 200 | 1 | 1/10 | R | 45588 | 5588 | 5587 | 0x03 | N | mA
Analog input 4 | INT16 | 2 | 1 | -200 | 200 | 1 | 1/10 | R | 45589 | 5589 | 5588 | 0x03 | N | mA
Reserved | INT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45590 | 5590 | 5589 | 0x03 | N | mA
Reserved | INT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45591 | 5591 | 5590 | 0x03 | N | mA
Reserved | INT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45592 | 5592 | 5591 | 0x03 | N | mA
Reserved | INT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45593 | 5593 | 5592 | 0x03 | N | mA
Analog output 1 | INT16 | 2 | 1 | 0 | 200 | 1 | 1/10 | R | 45594 | 5594 | 5593 | 0x03 | N | mA
Analog output 2 | INT16 | 2 | 1 | 0 | 200 | 1 | 1/10 | R | 45595 | 5595 | 5594 | 0x03 | N | mA
Reserved | INT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45596 | 5596 | 5595 | 0x03 | N | mA
Reserved | INT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 45597 | 5597 | 5596 | 0x03 | N | mA
Temperature Module Data
Temperature Input 1 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45598 | 5598 | 5597 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 2 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45599 | 5599 | 5598 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 3 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45600 | 5600 | 5599 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 4 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45601 | 5601 | 5600 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 5 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45602 | 5602 | 5601 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 6 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45603 | 5603 | 5602 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 7 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45604 | 5604 | 5603 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 8 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45605 | 5605 | 5604 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 9 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45606 | 5606 | 5605 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 10 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45607 | 5607 | 5606 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 11 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45608 | 5608 | 5607 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 12 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45609 | 5609 | 5608 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 13 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45610 | 5610 | 5609 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 14 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45611 | 5611 | 5610 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Temperature Input 15 | INT16 | 2 | 1 | -500 | 3000 | 1 | 1/10 | R | 45612 | 5612 | 5611 | 0x03 | N | °C or F |  | Refer the unit selected for temperature measurement
Boolean Data | [16 empty] | 72:06 | Hex
DI Status | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45626 | 5626 | 5625 | 0x03 | N |  |  |  | 1 | 1
DO Status | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45628 | 5628 | 5627 | 0x03 | N |  |  |  | 2 | 2
Custom Logic DI Status | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45630 | 5630 | 5629 | 0x03 | N |  |  | Bit 0:Local-START> DI Bit 1:Local-STOP DI Bit 2:Local-START>> DI Bit 3:Mode Selection 1 Bit 4:Local-START< DI Bit 5:Local-START<< DI Bit 6:Remote-START> DI Bit 7:Remote-STOP DI Bit 8:Remote-START>> DI Bit 9:Mode Selection 2 Bit 10:Remote-START< DI Bit 11:Remote-START<< DI Bit 12:Run DI Bit 13:Speed Change Bit 14:Not Used Bit 15:Not Used | 3 | 3
Reserved | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45631 | 5631 | 5630 | 0x03 | N |  |  |  | 4 | 4
Truth table | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45632 | 5632 | 5631 | 0x03 | N |  |  |  | 5 | 5
Timer Status | BITMAP | 2 | 1 | 0 | 15 | 1 | 1 | R | 45634 | 5634 | 5633 | 0x03 | N |  |  |  | 6 | 6
Counter Status | BITMAP | 2 | 1 | 0 | 15 | 1 | 1 | R | 45635 | 5635 | 5634 | 0x03 | N |  |  |  | 7 | 7
Signal Conditioner Status | BITMAP | 2 | 1 | 0 | 15 | 1 | 1 | R | 45636 | 5636 | 5635 | 0x03 | N |  |  |  | 8 | 8
Non-Volatile element status | BITMAP | 2 | 1 | 0 | 15 | 1 | 1 | R | 45637 | 5637 | 5636 | 0x03 | N |  |  |  | 9 | 9
Analog comparator Output Status | BITMAP | 2 | 1 | 0 | 15 | 1 | 1 | R | 45638 | 5638 | 5637 | 0x03 | N |  |  | Bit 0:Analog Comparatoring 1 Output Bit 1:Analog Comparatoring 2 Output Bit 2:Analog Comparatoring 3 Output Bit 3:Analog Comparatoring 4 Output | 10 | A
Reserved | BITMAP | 2 | 1 | 0 | 0 | 1 | 1 | R | 45639 | 5639 | 5638 | 0x03 | N |  |  |  | 11 | B
Motor Status(Alarm,pickup,trip) | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45640 | 5640 | 5639 | 0x03 | N |  |  |  | 12 | C
Motor status(stop, start, run, inhibit) | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45641 | 5641 | 5640 | 0x03 | N |  |  |  | 13 | D | 72:06
Alarm Bits | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45642 | 5642 | 5641 | 0x03 | N |  |  |  | 14 | E
Pickup Bits | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45644 | 5644 | 5643 | 0x03 | N |  |  |  | 15 | F
Trip Bits | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45646 | 5646 | 5645 | 0x03 | N |  |  |  | 16 | 10
Interlock Alarm Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45648 | 5648 | 5647 | 0x03 | N |  |  |  | 17 | 11
Interlock Pickup Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45649 | 5649 | 5648 | 0x03 | N |  |  |  | 18 | 12
Interlock Trip Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45650 | 5650 | 5649 | 0x03 | N |  |  |  | 19 | 13
Analogue Unit Alarm Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45651 | 5651 | 5650 | 0x03 | N |  |  |  | 20 | 14
Analogue Unit Pickup Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45652 | 5652 | 5651 | 0x03 | N |  |  |  | 21 | 15
Analogue Unit Trip Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45653 | 5653 | 5652 | 0x03 | N |  |  |  | 22 | 16
Temperature Unit Alarm Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45654 | 5654 | 5653 | 0x03 | N |  |  |  | 23 | 17
Temperature Unit Pickup Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45655 | 5655 | 5654 | 0x03 | N |  |  |  | 24 | 18
Temperature Unit Trip Bits | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45656 | 5656 | 5655 | 0x03 | N |  |  |  | 25 | 19
Starter Commands | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45657 | 5657 | 5656 | 0x03 | N |  |  |  | 26 | 1A
Motor Run Indicators | BITMAP | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45659 | 5659 | 5658 | 0x03 | N |  |  |  | 27 | 1B
Permissive command status | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45660 | 5660 | 5659 | 0x03 | N |  |  |  | 28 | 1C
Inhibit Status | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45662 | 5662 | 5661 | 0x03 | N |  |  |  | 29 | 1D
Device Inernal: MU | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45664 | 5664 | 5663 | 0x03 | N |  |  |  | 30 | 1E
Device Internal - CTVT | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45666 | 5666 | 5665 | 0x03 | N |  |  |  | 31 | 1F
Communication Status | BITMAP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45668 | 5668 | 5667 | 0x03 | N |  |  | bit 0:Comm Fail Bit 1: HMI Port - No Coomunication Bit 2: NTP Not working Bit 3: DHCP IP assignment Fail Bit 4: Port 1 Link Fail Bit 5: Port 2 Link Fail All others are reserved | 32 | 20
Statistic Data
Timer 1 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45751 | 5751 | 5750 | 0x03 | N | mSec
Timer 2 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45752 | 5752 | 5751 | 0x03 | N | mSec
Timer 3 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45753 | 5753 | 5752 | 0x03 | N | mSec
Timer 4 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45754 | 5754 | 5753 | 0x03 | N | mSec
Counter 1 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45755 | 5755 | 5754 | 0x03 | N
Counter 2 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45756 | 5756 | 5755 | 0x03 | N
Counter 3 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45757 | 5757 | 5756 | 0x03 | N
Counter 4 - Actual value | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45758 | 5758 | 5757 | 0x03 | N
Thermal Overload trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45759 | 5759 | 5758 | 0x03 | N
Locked rotor trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45760 | 5760 | 5759 | 0x03 | N
Stalled rotor trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45761 | 5761 | 5760 | 0x03 | N
Definite time overcurrent trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45762 | 5762 | 5761 | 0x03 | N
Normal inverse overcurrent trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45763 | 5763 | 5762 | 0x03 | N
Short time overcurrent trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45764 | 5764 | 5763 | 0x03 | N
Calculated ground trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45765 | 5765 | 5764 | 0x03 | N
Measured ground trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45766 | 5766 | 5765 | 0x03 | N
Under current trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45767 | 5767 | 5766 | 0x03 | N
Current imbalance trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45768 | 5768 | 5767 | 0x03 | N
Current phase loss trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45769 | 5769 | 5768 | 0x03 | N
Current phase reversal trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45770 | 5770 | 5769 | 0x03 | N
Under voltage trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45771 | 5771 | 5770 | 0x03 | N
Over voltage trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45772 | 5772 | 5771 | 0x03 | N
Voltage phase loss trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45773 | 5773 | 5772 | 0x03 | N
Voltage imbalance trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45774 | 5774 | 5773 | 0x03 | N
Voltage phase reversal trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45775 | 5775 | 5774 | 0x03 | N
Under Frequency trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45776 | 5776 | 5775 | 0x03 | N
Over frequency trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45777 | 5777 | 5776 | 0x03 | N
Excessive start time trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45778 | 5778 | 5777 | 0x03 | N
Communication loss trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45779 | 5779 | 5778 | 0x03 | N
Main unit Temperature trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45780 | 5780 | 5779 | 0x03 | N
Under Power trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45781 | 5781 | 5780 | 0x03 | N
Over Power trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45782 | 5782 | 5781 | 0x03 | N
Under Power factor trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45783 | 5783 | 5782 | 0x03 | N
RESERVED_5 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45784 | 5784 | 5783 | 0x03 | N
Device Internal trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45785 | 5785 | 5784 | 0x03 | N
HMI communication loss trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45786 | 5786 | 5785 | 0x03 | N
RESERVED_8 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45787 | 5787 | 5786 | 0x03 | N
RESERVED_9 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45788 | 5788 | 5787 | 0x03 | N
RESERVED_10 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45789 | 5789 | 5788 | 0x03 | N
RESERVED_11 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45790 | 5790 | 5789 | 0x03 | N
DI Interlock 1 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45791 | 5791 | 5790 | 0x03 | N
DI Interlock 2 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45792 | 5792 | 5791 | 0x03 | N
DI Interlock 3 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45793 | 5793 | 5792 | 0x03 | N
DI Interlock 4 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45794 | 5794 | 5793 | 0x03 | N
DI Interlock 5 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45795 | 5795 | 5794 | 0x03 | N
DI Interlock 6 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45796 | 5796 | 5795 | 0x03 | N
DI Interlock 7 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45797 | 5797 | 5796 | 0x03 | N
DI Interlock 8 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45798 | 5798 | 5797 | 0x03 | N
DI Interlock 9 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45799 | 5799 | 5798 | 0x03 | N
DI Interlock 10 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45800 | 5800 | 5799 | 0x03 | N
DI Interlock 11 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45801 | 5801 | 5800 | 0x03 | N
DI Interlock 12 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45802 | 5802 | 5801 | 0x03 | N
RESERVED_13 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45803 | 5803 | 5802 | 0x03 | N
RESERVED_14 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45804 | 5804 | 5803 | 0x03 | N
RESERVED_15 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45805 | 5805 | 5804 | 0x03 | N
RESERVED_16 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45806 | 5806 | 5805 | 0x03 | N
Temperature input 1 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45807 | 5807 | 5806 | 0x03 | N
Temperature input 2 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45808 | 5808 | 5807 | 0x03 | N
Temperature input 3 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45809 | 5809 | 5808 | 0x03 | N
Temperature input 4 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45810 | 5810 | 5809 | 0x03 | N
Temperature input 5 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45811 | 5811 | 5810 | 0x03 | N
Temperature input 6 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45812 | 5812 | 5811 | 0x03 | N
Temperature input 7 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45813 | 5813 | 5812 | 0x03 | N
Temperature input 8 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45814 | 5814 | 5813 | 0x03 | N
Temperature input 9 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45815 | 5815 | 5814 | 0x03 | N
Temperature input 10 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45816 | 5816 | 5815 | 0x03 | N
Temperature input 11 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45817 | 5817 | 5816 | 0x03 | N
Temperature input 12 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45818 | 5818 | 5817 | 0x03 | N
Temperature input 13 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45819 | 5819 | 5818 | 0x03 | N
Temperature input 14 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45820 | 5820 | 5819 | 0x03 | N
Temperature input 15 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45821 | 5821 | 5820 | 0x03 | N
RESERVED_17 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45822 | 5822 | 5821 | 0x03 | N
Analog Input 1 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45823 | 5823 | 5822 | 0x03 | N
Analog Input 2 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45824 | 5824 | 5823 | 0x03 | N
Analog Input 3 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45825 | 5825 | 5824 | 0x03 | N
Analog Input 4 trip Counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45826 | 5826 | 5825 | 0x03 | N
Calculator 1 Output | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45827 | 5827 | 5826 | 0x03 | N
Calculator 2 Output | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45828 | 5828 | 5827 | 0x03 | N
Motor stop error detection trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45829 | 5829 | 5828 | 0x03 | N
Logic test interrupted trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45830 | 5830 | 5829 | 0x03 | N
Stucked reset key trip counter | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45831 | 5831 | 5830 | 0x03 | N
Extended Monitoring Data
Status word 1 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45876 | 5876 | 5875 | 0x03 | N | -
Status word 2 | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45877 | 5877 | 5876 | 0x03 | N | -
L1 Current (%IFLC) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45878 | 5878 | 5877 | 0x03 | N | %IFLC
L2 Current (%IFLC) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45879 | 5879 | 5878 | 0x03 | N | %IFLC
L3 Current (%IFLC) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45880 | 5880 | 5879 | 0x03 | N | %IFLC
Calc Earth fault (%IFLC) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45881 | 5881 | 5880 | 0x03 | N | %IFLC
Average Current (%IFLC) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45882 | 5882 | 5881 | 0x03 | N | %IFLC
Maximum Current (Imax) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45883 | 5883 | 5882 | 0x03 | N | %IFLC
L1-L2 voltage / L1-N Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 45884 | 5884 | 5883 | 0x03 | N | V
L2-L3 Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 45885 | 5885 | 5884 | 0x03 | N | V
L3-L1 Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 45886 | 5886 | 5885 | 0x03 | N | V
Average Voltage | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1/10 | R | 45887 | 5887 | 5886 | 0x03 | N | V
Total RUN Hour | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45888 | 5888 | 5887 | 0x03 | N | Hr
Last RUN Hour | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45889 | 5889 | 5888 | 0x03 | N | Hr
Motor Starting Time | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45890 | 5890 | 5889 | 0x03 | N | Sec
Motor Starting current(%IFLC) | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45891 | 5891 | 5890 | 0x03 | N | %IFLC
Active Power | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45892 | 5892 | 5891 | 0x03 | N | KW
Reactive Power | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45893 | 5893 | 5892 | 0x03 | N | KVAR
Apparent power | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45894 | 5894 | 5893 | 0x03 | N | KVA
Active Energy | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45895 | 5895 | 5894 | 0x03 | N | KWH
Reactive Energy | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45897 | 5897 | 5896 | 0x03 | N | KVARh
Apparent Energy | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 45899 | 5899 | 5898 | 0x03 | N | KVAh
Mode status | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | R | 45901 | 5901 | 5900 | 0x03 | N |  | 0: Local1 1: Remote 2: Local2 3: Local3 | 0
Active trip count | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45902 | 5902 | 5901 | 0x03 | N
Active alarm count | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | R | 45903 | 5903 | 5902 | 0x03 | N |  |  | 0
Note on G32: Vrund Rana: range is 0-5720 for (F)fahrenheit

## Commands (hidden)
Attribute Name | Data Type | Size(in Bits) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units
Commands
Start > | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 1 | 1 | 0 | 0x01,0x05,0x0F | N | 0
Start >> | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 2 | 2 | 1 | 0x01,0x05,0x0F | N | 0
Stop | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 3 | 3 | 2 | 0x01,0x05,0x0F | N | 0
Start < | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 4 | 4 | 3 | 0x01,0x05,0x0F | N | 0
Start << | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 5 | 5 | 4 | 0x01,0x05,0x0F | N | 0
Trip reset | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 6 | 6 | 5 | 0x01,0x05,0x0F | N | 0
Inhibit reset (max starts) | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 7 | 7 | 6 | 0x01,0x05,0x0F | N | 0
Reset starts counter | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 8 | 8 | 7 | 0x01,0x05,0x0F | N | 0
Reset stops counter | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 9 | 9 | 8 | 0x01,0x05,0x0F | N | 0
Clear thermal memory | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 10 | 10 | 9 | 0x01,0x05,0x0F | N | 0
Reset total run hour | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 11 | 11 | 10 | 0x01,0x05,0x0F | N | 0
Reset energy | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 12 | 12 | 11 | 0x01,0x05,0x0F | N | 0
Emergancy start | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 13 | 13 | 12 | 0x01,0x05,0x0F | N | 0
Logic test input | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 14 | 14 | 13 | 0x01,0x05,0x0F | N | 0
Self test without trip | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 15 | 15 | 14 | 0x01,0x05,0x0F | N | 0
Self test with trip | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 16 | 16 | 15 | 0x01,0x05,0x0F | N | 0
Reset soft starter | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 17 | 17 | 16 | 0x01,0x05,0x0F | N | 0
Reset trip counter | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 18 | 18 | 17 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 19 | 19 | 18 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 20 | 20 | 19 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 21 | 21 | 20 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 22 | 22 | 21 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 23 | 23 | 22 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 24 | 24 | 23 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 25 | 25 | 24 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 26 | 26 | 25 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 27 | 27 | 26 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 28 | 28 | 27 | 0x01,0x05,0x0F | N | 0
Store Ref. Motor start record | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 29 | 29 | 28 | 0x01,0x05,0x0F | N | 0
Clear Fault Reports | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 30 | 30 | 29 | 0x01,0x05,0x0F | N | 0
Clear event records | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 31 | 31 | 30 | 0x01,0x05,0x0F | N | 0
Factory Reset | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 32 | 32 | 31 | 0x01,0x05,0x0F | N | 0
Permissive Commands
Permissive Command 1 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 33 | 33 | 32 | 0x01,0x05,0x0F | N | 0
Permissive Command 2 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 34 | 34 | 33 | 0x01,0x05,0x0F | N | 0
Permissive Command 3 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 35 | 35 | 34 | 0x01,0x05,0x0F | N | 0
Permissive Command 4 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 36 | 36 | 35 | 0x01,0x05,0x0F | N | 0
Permissive Command 5 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 37 | 37 | 36 | 0x01,0x05,0x0F | N | 0
Permissive Command 6 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 38 | 38 | 37 | 0x01,0x05,0x0F | N | 0
Permissive Command 7 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 39 | 39 | 38 | 0x01,0x05,0x0F | N | 0
Permissive Command 8 | BOOL | 1 | 0 | 1 | 1 | 1 | RW | 40 | 40 | 39 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 41 | 41 | 40 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 42 | 42 | 41 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 43 | 43 | 42 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 44 | 44 | 43 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 45 | 45 | 44 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 46 | 46 | 45 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 47 | 47 | 46 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 48 | 48 | 47 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 49 | 49 | 48 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 50 | 50 | 49 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 51 | 51 | 50 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 52 | 52 | 51 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 53 | 53 | 52 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 54 | 54 | 53 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 55 | 55 | 54 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 56 | 56 | 55 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 57 | 57 | 56 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 58 | 58 | 57 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 59 | 59 | 58 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 60 | 60 | 59 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 61 | 61 | 60 | 0x01,0x05,0x0F | N | 0
Reserved | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 62 | 62 | 61 | 0x01,0x05,0x0F | N | 0
Local/Remote Mode Sel 1 | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 63 | 63 | 62 | 0x01,0x05,0x0F | N | 0
Local/Remote Mode Sel 2 | BOOL | 1 | 0 | 0 | 0 | 0 | RW | 64 | 64 | 63 | 0x01,0x05,0x0F | N | 0
Note on B32: 0 = NO 1 = YES This Command sbould not be available in Modbus
Note on B33: 0 = NO 1 = YES This Command sbould not be available in Modbus
Note on B34: 0 = NO 1 = YES This Command sbould not be available in Modbus
Note on B35: 0 = NO 1 = YES This Command sbould not be available in Modbus
Note on B37: This Command is not applicable for display
Note on B38: This Command is not applicable for display
Note on B39: This Command is not applicable for display
Note on B40: This Command is not applicable for display
Note on B41: This Command is not applicable for display
Note on B42: This Command is not applicable for display
Note on B43: This Command is not applicable for display
Note on B44: This Command is not applicable for display

## Status
| Attribute Name | Data Type | Size(in Bits) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units
DI Status
| Digital Input 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10001 | 1 | 0 | 0x02 | N
| Digital Input 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10002 | 2 | 1 | 0x02 | N
| Digital Input 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10003 | 3 | 2 | 0x02 | N
| Digital Input 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10004 | 4 | 3 | 0x02 | N
| Digital Input 5 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10005 | 5 | 4 | 0x02 | N
| Digital Input 6 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10006 | 6 | 5 | 0x02 | N
| Digital Input 7 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10007 | 7 | 6 | 0x02 | N
| Digital Input 8 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10008 | 8 | 7 | 0x02 | N
| Digital Input 9 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10009 | 9 | 8 | 0x02 | N
| Digital Input 10 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10010 | 10 | 9 | 0x02 | N
| Digital Input 11 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10011 | 11 | 10 | 0x02 | N
| Digital Input 12 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10012 | 12 | 11 | 0x02 | N
| Digital Input 13 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10013 | 13 | 12 | 0x02 | N
| Digital Input 14 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10014 | 14 | 13 | 0x02 | N
| Digital Input 15 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10015 | 15 | 14 | 0x02 | N
| Digital Input 16 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10016 | 16 | 15 | 0x02 | N
| Digital Input 17 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10017 | 17 | 16 | 0x02 | N
| Digital Input 18 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10018 | 18 | 17 | 0x02 | N
| Digital Input 19 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10019 | 19 | 18 | 0x02 | N
| Digital Input 20 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10020 | 20 | 19 | 0x02 | N
| Digital Input 21 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10021 | 21 | 20 | 0x02 | N
| Digital Input 22 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10022 | 22 | 21 | 0x02 | N
| Digital Input 23 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10023 | 23 | 22 | 0x02 | N
| Digital Input 24 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10024 | 24 | 23 | 0x02 | N
| Digital Input 25 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10025 | 25 | 24 | 0x02 | N
| Digital Input 26 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10026 | 26 | 25 | 0x02 | N
| Digital Input 27 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10027 | 27 | 26 | 0x02 | N
| Digital Input 28 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10028 | 28 | 27 | 0x02 | N
| Digital Input 29 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10029 | 29 | 28 | 0x02 | N
| Digital Input 30 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10030 | 30 | 29 | 0x02 | N
| Digital Input 31 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10031 | 31 | 30 | 0x02 | N
| Digital Input 32 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10032 | 32 | 31 | 0x02 | N
DO Status
| Digital Output 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10033 | 33 | 32 | 0x02 | N
| Digital Output 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10034 | 34 | 33 | 0x02 | N
| Digital Output 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10035 | 35 | 34 | 0x02 | N
| Digital Output 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10036 | 36 | 35 | 0x02 | N
| Digital Output 5 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10037 | 37 | 36 | 0x02 | N
| Digital Output 6 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10038 | 38 | 37 | 0x02 | N
| Digital Output 7 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10039 | 39 | 38 | 0x02 | N
| Digital Output 8 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10040 | 40 | 39 | 0x02 | N
| Digital Output 9 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10041 | 41 | 40 | 0x02 | N
| Digital Output 10 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10042 | 42 | 41 | 0x02 | N
| Digital Output 11 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10043 | 43 | 42 | 0x02 | N
| Digital Output 12 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10044 | 44 | 43 | 0x02 | N
| Digital Output 13 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10045 | 45 | 44 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10046 | 46 | 45 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10047 | 47 | 46 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10048 | 48 | 47 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10049 | 49 | 48 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10050 | 50 | 49 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10051 | 51 | 50 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10052 | 52 | 51 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10053 | 53 | 52 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10054 | 54 | 53 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10055 | 55 | 54 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10056 | 56 | 55 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10057 | 57 | 56 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10058 | 58 | 57 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10059 | 59 | 58 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10060 | 60 | 59 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10061 | 61 | 60 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10062 | 62 | 61 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10063 | 63 | 62 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10064 | 64 | 63 | 0x02 | N
Custom Logic DI status
| Local-START> DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10065 | 65 | 64 | 0x02 | N
| Local-STOP DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10066 | 66 | 65 | 0x02 | N
| Local-START>> DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10067 | 67 | 66 | 0x02 | N
| Mode Selection 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10068 | 68 | 67 | 0x02 | N
| Local-START< DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10069 | 69 | 68 | 0x02 | N
| Local-START<< DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10070 | 70 | 69 | 0x02 | N
| Remote-START> DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10071 | 71 | 70 | 0x02 | N
| Remote-STOP DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10072 | 72 | 71 | 0x02 | N
| Remote-START>> DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10073 | 73 | 72 | 0x02 | N
| Mode Selection 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10074 | 74 | 73 | 0x02 | N
| Remote-START< DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10075 | 75 | 74 | 0x02 | N
| Remote-START<< DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10076 | 76 | 75 | 0x02 | N
| Run DI | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10077 | 77 | 76 | 0x02 | N
| Speed Change | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10078 | 78 | 77 | 0x02 | N
| Not Used | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10079 | 79 | 78 | 0x02 | N
| Not Used | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10080 | 80 | 79 | 0x02 | N
Reserved
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10081 | 81 | 80 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10082 | 82 | 81 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10083 | 83 | 82 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10084 | 84 | 83 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10085 | 85 | 84 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10086 | 86 | 85 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10087 | 87 | 86 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10088 | 88 | 87 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10089 | 89 | 88 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10090 | 90 | 89 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10091 | 91 | 90 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10092 | 92 | 91 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10093 | 93 | 92 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10094 | 94 | 93 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10095 | 95 | 94 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10096 | 96 | 95 | 0x02 | N
Comp Logic - Truth Table Output
| 2IP_1OP_TT1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10097 | 97 | 96 | 0x02 | N
| 2IP_1OP_TT2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10098 | 98 | 97 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10099 | 99 | 98 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10100 | 100 | 99 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10101 | 101 | 100 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10102 | 102 | 101 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10103 | 103 | 102 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10104 | 104 | 103 | 0x02 | N
| 3IP_1OP_TT1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10105 | 105 | 104 | 0x02 | N
| 3IP_1OP_TT2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10106 | 106 | 105 | 0x02 | N
| 3IP_1OP_TT3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10107 | 107 | 106 | 0x02 | N
| 3IP_1OP_TT4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10108 | 108 | 107 | 0x02 | N
| 3IP_1OP_TT5 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10109 | 109 | 108 | 0x02 | N
| 3IP_1OP_TT6 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10110 | 110 | 109 | 0x02 | N
| 3IP_1OP_TT7 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10111 | 111 | 110 | 0x02 | N
| 3IP_1OP_TT8 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10112 | 112 | 111 | 0x02 | N
| 5IP_2OP_TT1_OP1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10113 | 113 | 112 | 0x02 | N
| 5IP_2OP_TT1_OP2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10114 | 114 | 113 | 0x02 | N
| 5IP_2OP_TT2_OP1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10115 | 115 | 114 | 0x02 | N
| 5IP_2OP_TT2_OP2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10116 | 116 | 115 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10117 | 117 | 116 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10118 | 118 | 117 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10119 | 119 | 118 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10120 | 120 | 119 | 0x02 | N
| 4IP_1OP_TT1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10121 | 121 | 120 | 0x02 | N
| 4IP_1OP_TT2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10122 | 122 | 121 | 0x02 | N
| 4IP_1OP_TT3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10123 | 123 | 122 | 0x02 | N
| 4IP_1OP_TT4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10124 | 124 | 123 | 0x02 | N
| 4IP_1OP_TT5 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10125 | 125 | 124 | 0x02 | N
| 4IP_1OP_TT6 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10126 | 126 | 125 | 0x02 | N
| 4IP_1OP_TT7 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10127 | 127 | 126 | 0x02 | N
| 4IP_1OP_TT8 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10128 | 128 | 127 | 0x02 | N
Comp Logic - Timer Output
| Timer OP 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10129 | 129 | 128 | 0x02 | N
| Timer OP 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10130 | 130 | 129 | 0x02 | N
| Timer OP 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10131 | 131 | 130 | 0x02 | N
| Timer OP 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10132 | 132 | 131 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10133 | 133 | 132 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10134 | 134 | 133 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10135 | 135 | 134 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10136 | 136 | 135 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10137 | 137 | 136 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10138 | 138 | 137 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10139 | 139 | 138 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10140 | 140 | 139 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10141 | 141 | 140 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10142 | 142 | 141 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10143 | 143 | 142 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10144 | 144 | 143 | 0x02 | N
Comp Logic - Counter Output
| Counter OP 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10145 | 145 | 144 | 0x02 | N
| Counter OP 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10146 | 146 | 145 | 0x02 | N
| Counter OP 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10147 | 147 | 146 | 0x02 | N
| Counter OP 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10148 | 148 | 147 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10149 | 149 | 148 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10150 | 150 | 149 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10151 | 151 | 150 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10152 | 152 | 151 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10153 | 153 | 152 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10154 | 154 | 153 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10155 | 155 | 154 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10156 | 156 | 155 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10157 | 157 | 156 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10158 | 158 | 157 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10159 | 159 | 158 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10160 | 160 | 159 | 0x02 | N
Comp Logic - Signal Conditioner Output
| Signal Conditioner OP 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10161 | 161 | 160 | 0x02 | N
| Signal Conditioner OP 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10162 | 162 | 161 | 0x02 | N
| Signal Conditioner OP 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10163 | 163 | 162 | 0x02 | N
| Signal Conditioner OP 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10164 | 164 | 163 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10165 | 165 | 164 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10166 | 166 | 165 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10167 | 167 | 166 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10168 | 168 | 167 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10169 | 169 | 168 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10170 | 170 | 169 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10171 | 171 | 170 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10172 | 172 | 171 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10173 | 173 | 172 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10174 | 174 | 173 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10175 | 175 | 174 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10176 | 176 | 175 | 0x02 | N
Comp Logic - NV Element Output
| Non Volatile Element OP 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10177 | 177 | 176 | 0x02 | N
| Non Volatile Element OP 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10178 | 178 | 177 | 0x02 | N
| Non Volatile Element OP 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10179 | 179 | 178 | 0x02 | N
| Non Volatile Element OP 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10180 | 180 | 179 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10181 | 181 | 180 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10182 | 182 | 181 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10183 | 183 | 182 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10184 | 184 | 183 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10185 | 185 | 184 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10186 | 186 | 185 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10187 | 187 | 186 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10188 | 188 | 187 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10189 | 189 | 188 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10190 | 190 | 189 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10191 | 191 | 190 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10192 | 192 | 191 | 0x02 | N
Analog Comparator Output
| Analog Comparator OP 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10193 | 193 | 192 | 0x02 | N
| Analog Comparator OP 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10194 | 194 | 193 | 0x02 | N
| Analog Comparator OP 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10195 | 195 | 194 | 0x02 | N
| Analog Comparator OP 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10196 | 196 | 195 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10197 | 197 | 196 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10198 | 198 | 197 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10199 | 199 | 198 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10200 | 200 | 199 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10201 | 201 | 200 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10202 | 202 | 201 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10203 | 203 | 202 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10204 | 204 | 203 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10205 | 205 | 204 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10206 | 206 | 205 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10207 | 207 | 206 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10208 | 208 | 207 | 0x02 | N
Reserved
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10209 | 209 | 208 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10210 | 210 | 209 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10211 | 211 | 210 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10212 | 212 | 211 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10213 | 213 | 212 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10214 | 214 | 213 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10215 | 215 | 214 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10216 | 216 | 215 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10217 | 217 | 216 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10218 | 218 | 217 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10219 | 219 | 218 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10220 | 220 | 219 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10221 | 221 | 220 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10222 | 222 | 221 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10223 | 223 | 222 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10224 | 224 | 223 | 0x02 | N
Common Trip, Alarm and Pickup Status
| Pickup Status | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10225 | 225 | 224 | 0x02 | N
| Alarm Status | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10226 | 226 | 225 | 0x02 | N
| Trip Status | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10227 | 227 | 226 | 0x02 | N
| Motor stop error detection trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10228 | 228 | 227 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10229 | 229 | 228 | 0x02 | N
| Block Output | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10230 | 230 | 229 | 0x02 | N
| Logic test interrupted trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10231 | 231 | 230 | 0x02 | N
| Logic test interrupted pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10232 | 232 | 231 | 0x02 | N
| Stucked reset key trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10233 | 233 | 232 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10234 | 234 | 233 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10235 | 235 | 234 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10236 | 236 | 235 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10237 | 237 | 236 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10238 | 238 | 237 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10239 | 239 | 238 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10240 | 240 | 239 | 0x02 | N
Motor Status
| Motor Stop | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10241 | 241 | 240 | 0x02 | N
| Motor Start | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10242 | 242 | 241 | 0x02 | N
| Motor Run | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10243 | 243 | 242 | 0x02 | N
| Motor Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10244 | 244 | 243 | 0x02 | N
| Remote Mode | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10245 | 245 | 244 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10246 | 246 | 245 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10247 | 247 | 246 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10248 | 248 | 247 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10249 | 249 | 248 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10250 | 250 | 249 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10251 | 251 | 250 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10252 | 252 | 251 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10253 | 253 | 252 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10254 | 254 | 253 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10255 | 255 | 254 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10256 | 256 | 255 | 0x02 | N
Protection Alarm Status
| Thermal Overload Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10257 | 257 | 256 | 0x02 | N
| Locked Rotor Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10258 | 258 | 257 | 0x02 | N
| Stalled Rotor Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10259 | 259 | 258 | 0x02 | N
| Definite time overcurrent Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10260 | 260 | 259 | 0x02 | N
| Normal inverse overcurrent Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10261 | 261 | 260 | 0x02 | N
| Short time overcurrent Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10262 | 262 | 261 | 0x02 | N
| Calculated ground current Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10263 | 263 | 262 | 0x02 | N
| Measured ground current Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10264 | 264 | 263 | 0x02 | N
| Under Current Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10265 | 265 | 264 | 0x02 | N
| Current Imbalance Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10266 | 266 | 265 | 0x02 | N
| Current Phase Loss Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10267 | 267 | 266 | 0x02 | N
| Current Phase Reversal Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10268 | 268 | 267 | 0x02 | N
| Under Voltage Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10269 | 269 | 268 | 0x02 | N
| Over Voltage Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10270 | 270 | 269 | 0x02 | N
| Voltage Phase Loss Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10271 | 271 | 270 | 0x02 | N
| Voltage Imbalance Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10272 | 272 | 271 | 0x02 | N
| Voltage Phase Reversal Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10273 | 273 | 272 | 0x02 | N
| Under Frequency Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10274 | 274 | 273 | 0x02 | N
| Over Frequency Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10275 | 275 | 274 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10276 | 276 | 275 | 0x02 | N
| Communication loss Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10277 | 277 | 276 | 0x02 | N
| Over Temperature Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10278 | 278 | 277 | 0x02 | N
| Under Power Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10279 | 279 | 278 | 0x02 | N
| Over Power Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10280 | 280 | 279 | 0x02 | N
| Under Power factor Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10281 | 281 | 280 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10282 | 282 | 281 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10283 | 283 | 282 | 0x02 | N
| HMI communication loss alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10284 | 284 | 283 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10285 | 285 | 284 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10286 | 286 | 285 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10287 | 287 | 286 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10288 | 288 | 287 | 0x02 | N
Protection Pickup Status
| Thermal Overload Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10289 | 289 | 288 | 0x02 | N
| Locked Rotor Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10290 | 290 | 289 | 0x02 | N
| Stalled Rotor Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10291 | 291 | 290 | 0x02 | N
| Definite time overcurrent Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10292 | 292 | 291 | 0x02 | N
| Normal inverse overcurrent Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10293 | 293 | 292 | 0x02 | N
| Short time overcurrent Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10294 | 294 | 293 | 0x02 | N
| Calculated ground current Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10295 | 295 | 294 | 0x02 | N
| Measured ground current Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10296 | 296 | 295 | 0x02 | N
| Under Current Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10297 | 297 | 296 | 0x02 | N
| Current Imbalance Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10298 | 298 | 297 | 0x02 | N
| Current Phase Loss Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10299 | 299 | 298 | 0x02 | N
| Current Phase Reversal Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10300 | 300 | 299 | 0x02 | N
| Under Voltage Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10301 | 301 | 300 | 0x02 | N
| Over Voltage Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10302 | 302 | 301 | 0x02 | N
| Voltage Phase Loss Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10303 | 303 | 302 | 0x02 | N
| Voltage Imbalance Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10304 | 304 | 303 | 0x02 | N
| Voltage Phase Reversal Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10305 | 305 | 304 | 0x02 | N
| Under Frequency Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10306 | 306 | 305 | 0x02 | N
| Over Frequency Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10307 | 307 | 306 | 0x02 | N
Excessive Start time pickup | Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10308 | 308 | 307 | 0x02 | N
| Communication loss Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10309 | 309 | 308 | 0x02 | N
| Over Temperature Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10310 | 310 | 309 | 0x02 | N
| Under Power Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10311 | 311 | 310 | 0x02 | N
| Over Power Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10312 | 312 | 311 | 0x02 | N
| Under Power factor Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10313 | 313 | 312 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10314 | 314 | 313 | 0x02 | N
| Internal Controller Malfunction (ICM) Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10315 | 315 | 314 | 0x02 | N
| HMI communication loss Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10316 | 316 | 315 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10317 | 317 | 316 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10318 | 318 | 317 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10319 | 319 | 318 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10320 | 320 | 319 | 0x02 | N
Protection Trip Status
| Thermal Overload Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10321 | 321 | 320 | 0x02 | N
| Locked Rotor Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10322 | 322 | 321 | 0x02 | N
| Stalled Rotor Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10323 | 323 | 322 | 0x02 | N
| Definite time overcurrent Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10324 | 324 | 323 | 0x02 | N
| Normal inverse overcurrent Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10325 | 325 | 324 | 0x02 | N
| Short time overcurrent Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10326 | 326 | 325 | 0x02 | N
| Calculated ground current Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10327 | 327 | 326 | 0x02 | N
| Measured ground current Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10328 | 328 | 327 | 0x02 | N
| Under Current Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10329 | 329 | 328 | 0x02 | N
| Current Imbalance Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10330 | 330 | 329 | 0x02 | N
| Current Phase Loss Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10331 | 331 | 330 | 0x02 | N
| Current Phase Reversal Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10332 | 332 | 331 | 0x02 | N
| Under Voltage Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10333 | 333 | 332 | 0x02 | N
| Over Voltage Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10334 | 334 | 333 | 0x02 | N
| Voltage Phase Loss Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10335 | 335 | 334 | 0x02 | N
| Voltage Imbalance Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10336 | 336 | 335 | 0x02 | N
| Voltage Phase Reversal Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10337 | 337 | 336 | 0x02 | N
| Under Frequency Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10338 | 338 | 337 | 0x02 | N
| Over Frequency Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10339 | 339 | 338 | 0x02 | N
Excessive start time trip | Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10340 | 340 | 339 | 0x02 | N
| Communication loss Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10341 | 341 | 340 | 0x02 | N
| Over Temperature Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10342 | 342 | 341 | 0x02 | N
| Under Power Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10343 | 343 | 342 | 0x02 | N
| Over Power Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10344 | 344 | 343 | 0x02 | N
| Under Power factor Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10345 | 345 | 344 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10346 | 346 | 345 | 0x02 | N
| Internal Controller Malfunction (ICM) Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10347 | 347 | 346 | 0x02 | N
| HMI communication loss trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10348 | 348 | 347 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10349 | 349 | 348 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10350 | 350 | 349 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10351 | 351 | 350 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10352 | 352 | 351 | 0x02 | N
Interlock Protection Alarm Status
| Interlock 1 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10353 | 353 | 352 | 0x02 | N
| Interlock 2 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10354 | 354 | 353 | 0x02 | N
| Interlock 3 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10355 | 355 | 354 | 0x02 | N
| Interlock 4 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10356 | 356 | 355 | 0x02 | N
| Interlock 5 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10357 | 357 | 356 | 0x02 | N
| Interlock 6 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10358 | 358 | 357 | 0x02 | N
| Interlock 7 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10359 | 359 | 358 | 0x02 | N
| Interlock 8 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10360 | 360 | 359 | 0x02 | N
| Interlock 9 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10361 | 361 | 360 | 0x02 | N
| Interlock 10 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10362 | 362 | 361 | 0x02 | N
| Interlock 11 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10363 | 363 | 362 | 0x02 | N
| Interlock 12 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10364 | 364 | 363 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10365 | 365 | 364 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10366 | 366 | 365 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10367 | 367 | 366 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10368 | 368 | 367 | 0x02 | N
Interlock Protection Pickup Status
| Interlock 1 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10369 | 369 | 368 | 0x02 | N
| Interlock 2 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10370 | 370 | 369 | 0x02 | N
| Interlock 3 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10371 | 371 | 370 | 0x02 | N
| Interlock 4 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10372 | 372 | 371 | 0x02 | N
| Interlock 5 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10373 | 373 | 372 | 0x02 | N
| Interlock 6 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10374 | 374 | 373 | 0x02 | N
| Interlock 7 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10375 | 375 | 374 | 0x02 | N
| Interlock 8 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10376 | 376 | 375 | 0x02 | N
| Interlock 9 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10377 | 377 | 376 | 0x02 | N
| Interlock 10 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10378 | 378 | 377 | 0x02 | N
| Interlock 11 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10379 | 379 | 378 | 0x02 | N
| Interlock 12 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10380 | 380 | 379 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10381 | 381 | 380 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10382 | 382 | 381 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10383 | 383 | 382 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10384 | 384 | 383 | 0x02 | N
Interlock Protection Trip Status
| Interlock 1 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10385 | 385 | 384 | 0x02 | N
| Interlock 2 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10386 | 386 | 385 | 0x02 | N
| Interlock 3 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10387 | 387 | 386 | 0x02 | N
| Interlock 4 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10388 | 388 | 387 | 0x02 | N
| Interlock 5 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10389 | 389 | 388 | 0x02 | N
| Interlock 6 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10390 | 390 | 389 | 0x02 | N
| Interlock 7 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10391 | 391 | 390 | 0x02 | N
| Interlock 8 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10392 | 392 | 391 | 0x02 | N
| Interlock 9 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10393 | 393 | 392 | 0x02 | N
| Interlock 10 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10394 | 394 | 393 | 0x02 | N
| Interlock 11 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10395 | 395 | 394 | 0x02 | N
| Interlock 12 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10396 | 396 | 395 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10397 | 397 | 396 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10398 | 398 | 397 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10399 | 399 | 398 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10400 | 400 | 399 | 0x02 | N
Analog Protection Alarm Status
| AI1 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10401 | 401 | 400 | 0x02 | N
| AI2 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10402 | 402 | 401 | 0x02 | N
| AI3 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10403 | 403 | 402 | 0x02 | N
| AI4 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10404 | 404 | 403 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10405 | 405 | 404 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10406 | 406 | 405 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10407 | 407 | 406 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10408 | 408 | 407 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10409 | 409 | 408 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10410 | 410 | 409 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10411 | 411 | 410 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10412 | 412 | 411 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10413 | 413 | 412 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10414 | 414 | 413 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10415 | 415 | 414 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10416 | 416 | 415 | 0x02 | N
Analog Protection Pickup Status
| AI1 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10417 | 417 | 416 | 0x02 | N
| AI2 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10418 | 418 | 417 | 0x02 | N
| AI3 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10419 | 419 | 418 | 0x02 | N
| AI4 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10420 | 420 | 419 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10421 | 421 | 420 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10422 | 422 | 421 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10423 | 423 | 422 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10424 | 424 | 423 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10425 | 425 | 424 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10426 | 426 | 425 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10427 | 427 | 426 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10428 | 428 | 427 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10429 | 429 | 428 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10430 | 430 | 429 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10431 | 431 | 430 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10432 | 432 | 431 | 0x02 | N
Analog Protection Trip Status
| AI1 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10433 | 433 | 432 | 0x02 | N
| AI2 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10434 | 434 | 433 | 0x02 | N
| AI3 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10435 | 435 | 434 | 0x02 | N
| AI4 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10436 | 436 | 435 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10437 | 437 | 436 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10438 | 438 | 437 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10439 | 439 | 438 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10440 | 440 | 439 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10441 | 441 | 440 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10442 | 442 | 441 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10443 | 443 | 442 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10444 | 444 | 443 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10445 | 445 | 444 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10446 | 446 | 445 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10447 | 447 | 446 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10448 | 448 | 447 | 0x02 | N
Temperature Protection Alarm Status
| TI1 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10449 | 449 | 448 | 0x02 | N
| TI2 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10450 | 450 | 449 | 0x02 | N
| TI3 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10451 | 451 | 450 | 0x02 | N
| TI4 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10452 | 452 | 451 | 0x02 | N
| TI5 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10453 | 453 | 452 | 0x02 | N
| TI6 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10454 | 454 | 453 | 0x02 | N
| TI7 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10455 | 455 | 454 | 0x02 | N
| TI8 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10456 | 456 | 455 | 0x02 | N
| TI9 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10457 | 457 | 456 | 0x02 | N
| TI10 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10458 | 458 | 457 | 0x02 | N
| TI11 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10459 | 459 | 458 | 0x02 | N
| TI12 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10460 | 460 | 459 | 0x02 | N
| TI13 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10461 | 461 | 460 | 0x02 | N
| TI14 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10462 | 462 | 461 | 0x02 | N
| TI15 Alarm | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10463 | 463 | 462 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10464 | 464 | 463 | 0x02 | N
Temperature Protection Pickup Status
| TI1 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10465 | 465 | 464 | 0x02 | N
| TI2 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10466 | 466 | 465 | 0x02 | N
| TI3 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10467 | 467 | 466 | 0x02 | N
| TI4 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10468 | 468 | 467 | 0x02 | N
| TI5 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10469 | 469 | 468 | 0x02 | N
| TI6 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10470 | 470 | 469 | 0x02 | N
| TI7 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10471 | 471 | 470 | 0x02 | N
| TI8 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10472 | 472 | 471 | 0x02 | N
| TI9 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10473 | 473 | 472 | 0x02 | N
| TI10 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10474 | 474 | 473 | 0x02 | N
| TI11 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10475 | 475 | 474 | 0x02 | N
| TI12 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10476 | 476 | 475 | 0x02 | N
| TI13 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10477 | 477 | 476 | 0x02 | N
| TI14 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10478 | 478 | 477 | 0x02 | N
| TI15 Pickup | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10479 | 479 | 478 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10480 | 480 | 479 | 0x02 | N
Temperature Protection Trip Status
| TI1 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10481 | 481 | 480 | 0x02 | N
| TI2 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10482 | 482 | 481 | 0x02 | N
| TI3 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10483 | 483 | 482 | 0x02 | N
| TI4 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10484 | 484 | 483 | 0x02 | N
| TI5 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10485 | 485 | 484 | 0x02 | N
| TI6 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10486 | 486 | 485 | 0x02 | N
| TI7 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10487 | 487 | 486 | 0x02 | N
| TI8 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10488 | 488 | 487 | 0x02 | N
| TI9 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10489 | 489 | 488 | 0x02 | N
| TI10 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10490 | 490 | 489 | 0x02 | N
| TI11 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10491 | 491 | 490 | 0x02 | N
| TI12 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10492 | 492 | 491 | 0x02 | N
| TI13 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10493 | 493 | 492 | 0x02 | N
| TI14 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10494 | 494 | 493 | 0x02 | N
| TI15 Trip | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10495 | 495 | 494 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10496 | 496 | 495 | 0x02 | N
Comp Logic - Motor Starter Output
| CONTACTOR OUTPUT 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10497 | 497 | 496 | 0x02 | N
| CONTACTOR OUTPUT 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10498 | 498 | 497 | 0x02 | N
| CONTACTOR OUTPUT 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10499 | 499 | 498 | 0x02 | N
| CONTACTOR OUTPUT 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10500 | 500 | 499 | 0x02 | N
| CONTACTOR OUTPUT 5 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10501 | 501 | 500 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10502 | 502 | 501 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10503 | 503 | 502 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10504 | 504 | 503 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10505 | 505 | 504 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10506 | 506 | 505 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10507 | 507 | 506 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10508 | 508 | 507 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10509 | 509 | 508 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10510 | 510 | 509 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10511 | 511 | 510 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10512 | 512 | 511 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10513 | 513 | 512 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10514 | 514 | 513 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10515 | 515 | 514 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10516 | 516 | 515 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10517 | 517 | 516 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10518 | 518 | 517 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10519 | 519 | 518 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10520 | 520 | 519 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10521 | 521 | 520 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10522 | 522 | 521 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10523 | 523 | 522 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10524 | 524 | 523 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10525 | 525 | 524 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10526 | 526 | 525 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10527 | 527 | 526 | 0x02 | N
| Motor Stop | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10528 | 528 | 527 | 0x02 | N
Comp Logic - Motor Indicators
| Motor forward running | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10529 | 529 | 528 | 0x02 | N
| Motor reverse running | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10530 | 530 | 529 | 0x02 | N
| Motor fast forward running | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10531 | 531 | 530 | 0x02 | N
| Motor fast reverse running | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10532 | 532 | 531 | 0x02 | N
| Motor running in star (Forward) | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10533 | 533 | 532 | 0x02 | N
| Motor running in delta (Forward) | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10534 | 534 | 533 | 0x02 | N
| Motor running in star (Reverse) | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10535 | 535 | 534 | 0x02 | N
| Motor running in delta (Reverse) | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10536 | 536 | 535 | 0x02 | N
| Motor in star-delta changeover (forward) | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10537 | 537 | 536 | 0x02 | N
| Motor in star-delta changeover (reverse) | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10538 | 538 | 537 | 0x02 | N
| Interlocking time active | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10539 | 539 | 538 | 0x02 | N
| Change-over pause active | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10540 | 540 | 539 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10541 | 541 | 540 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10542 | 542 | 541 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10543 | 543 | 542 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10544 | 544 | 543 | 0x02 | N
Comp Logic - Pemissive Commands Status
| Status - Permissive Command 1 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10545 | 545 | 544 | 0x02 | N
| Status - Permissive Command 2 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10546 | 546 | 545 | 0x02 | N
| Status - Permissive Command 3 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10547 | 547 | 546 | 0x02 | N
| Status - Permissive Command 4 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10548 | 548 | 547 | 0x02 | N
| Status - Permissive Command 5 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10549 | 549 | 548 | 0x02 | N
| Status - Permissive Command 6 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10550 | 550 | 549 | 0x02 | N
| Status - Permissive Command 7 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10551 | 551 | 550 | 0x02 | N
| Status - Permissive Command 8 | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10552 | 552 | 551 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10553 | 553 | 552 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10554 | 554 | 553 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10555 | 555 | 554 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10556 | 556 | 555 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10557 | 557 | 556 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10558 | 558 | 557 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10559 | 559 | 558 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10560 | 560 | 559 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10561 | 561 | 560 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10562 | 562 | 561 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10563 | 563 | 562 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10564 | 564 | 563 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10565 | 565 | 564 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10566 | 566 | 565 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10567 | 567 | 566 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10568 | 568 | 567 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10569 | 569 | 568 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10570 | 570 | 569 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10571 | 571 | 570 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10572 | 572 | 571 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10573 | 573 | 572 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10574 | 574 | 573 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10575 | 575 | 574 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10576 | 576 | 575 | 0x02 | N
Comp Logic - Inhibit Status
| No Voltage Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10577 | 577 | 576 | 0x02 | N
| Under Voltage Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10578 | 578 | 577 | 0x02 | N
| Trip Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10579 | 579 | 578 | 0x02 | N
| Thermal Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10580 | 580 | 579 | 0x02 | N
| Max Starts Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10581 | 581 | 580 | 0x02 | N
| Interlock 1 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10582 | 582 | 581 | 0x02 | N
| Interlock 2 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10583 | 583 | 582 | 0x02 | N
| Interlock 3 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10584 | 584 | 583 | 0x02 | N
| Interlock 4 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10585 | 585 | 584 | 0x02 | N
| Interlock 5 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10586 | 586 | 585 | 0x02 | N
| Interlock 6 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10587 | 587 | 586 | 0x02 | N
| Interlock 7 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10588 | 588 | 587 | 0x02 | N
| Interlock 8 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10589 | 589 | 588 | 0x02 | N
| Interlock 9 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10590 | 590 | 589 | 0x02 | N
| Interlock 10 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10591 | 591 | 590 | 0x02 | N
| Interlock 11 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10592 | 592 | 591 | 0x02 | N
| Interlock 12 Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10593 | 593 | 592 | 0x02 | N
| Local DI Stop Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10594 | 594 | 593 | 0x02 | N
| Remote DI Stop Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10595 | 595 | 594 | 0x02 | N
| Communication Stop Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10596 | 596 | 595 | 0x02 | N
| Force Stop Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10597 | 597 | 596 | 0x02 | N
| Antibackspin Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10598 | 598 | 597 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10599 | 599 | 598 | 0x02 | N
| Direction change Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10600 | 600 | 599 | 0x02 | N
| Speed change Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10601 | 601 | 600 | 0x02 | N
| Custom Stop Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10602 | 602 | 601 | 0x02 | N
| Firmware Update Inhibit | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10603 | 603 | 602 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10604 | 604 | 603 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10605 | 605 | 604 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10606 | 606 | 605 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10607 | 607 | 606 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10608 | 608 | 607 | 0x02 | N
Internal controller malfunction detection - Main Controller
| Sensor module communication error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10609 | 609 | 608 | 0x02 | N
| Expansion module communication error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10610 | 610 | 609 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10611 | 611 | 610 | 0x02 | N
| EEPROM interface error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10612 | 612 | 611 | 0x02 | N
| EEPROM checksum error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10613 | 613 | 612 | 0x02 | N
| Configuration error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10614 | 614 | 613 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10615 | 615 | 614 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10616 | 616 | 615 | 0x02 | N
| Watchdog timeout detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10617 | 617 | 616 | 0x02 | N
| reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10618 | 618 | 617 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10619 | 619 | 618 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10620 | 620 | 619 | 0x02 | N
| Energy Register Overflow | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10621 | 621 | 620 | 0x02 | N
| Error detected during expansion module initialization | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10622 | 622 | 621 | 0x02 | N
| reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10623 | 623 | 622 | 0x02 | N
| Write Pub Key failure | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10624 | 624 | 623 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10625 | 625 | 624 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10626 | 626 | 625 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10627 | 627 | 626 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10628 | 628 | 627 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10629 | 629 | 628 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10630 | 630 | 629 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10631 | 631 | 630 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10632 | 632 | 631 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10633 | 633 | 632 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10634 | 634 | 633 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10635 | 635 | 634 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10636 | 636 | 635 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10637 | 637 | 636 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10638 | 638 | 637 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10639 | 639 | 638 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10640 | 640 | 639 | 0x02 | N
Internal controller malfunction detection - Sensor Module
| Watchdog timeout detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10641 | 641 | 640 | 0x02 | N
| ADC conversion error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10642 | 642 | 641 | 0x02 | N
| Flash error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10643 | 643 | 642 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10644 | 644 | 643 | 0x02 | N
| Voltage configuration not detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10645 | 645 | 644 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10646 | 646 | 645 | 0x02 | N
| Calibration error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10647 | 647 | 646 | 0x02 | N
| VL1 measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10648 | 648 | 647 | 0x02 | N
| VL2 measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10649 | 649 | 648 | 0x02 | N
| VL3 measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10650 | 650 | 649 | 0x02 | N
| IL1 low gain measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10651 | 651 | 650 | 0x02 | N
| IL1 high gain measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10652 | 652 | 651 | 0x02 | N
| IL2 low gain measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10653 | 653 | 652 | 0x02 | N
| IL2 high gain measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10654 | 654 | 653 | 0x02 | N
| IL3 low gain measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10655 | 655 | 654 | 0x02 | N
| IL3 high gain measurement error detected | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10656 | 656 | 655 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10657 | 657 | 656 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10658 | 658 | 657 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10659 | 659 | 658 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10660 | 660 | 659 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10661 | 661 | 660 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10662 | 662 | 661 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10663 | 663 | 662 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10664 | 664 | 663 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10665 | 665 | 664 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10666 | 666 | 665 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10667 | 667 | 666 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10668 | 668 | 667 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10669 | 669 | 668 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10670 | 670 | 669 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10671 | 671 | 670 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10672 | 672 | 671 | 0x02 | N
Communication Status
| ETH port Comm Fail | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10673 | 673 | 672 | 0x02 | N
| HMI Port - No Coomunication | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10674 | 674 | 673 | 0x02 | N
| NTP Not working | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10675 | 675 | 674 | 0x02 | N
| DHCP IP assignment Fail | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10676 | 676 | 675 | 0x02 | N
| Port 1 Link Fail | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10677 | 677 | 676 | 0x02 | N
| Port 2 Link Fail | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10678 | 678 | 677 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10679 | 679 | 678 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10680 | 680 | 679 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10681 | 681 | 680 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10682 | 682 | 681 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10683 | 683 | 682 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10684 | 684 | 683 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10685 | 685 | 684 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10686 | 686 | 685 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10687 | 687 | 686 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10688 | 688 | 687 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10689 | 689 | 688 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10690 | 690 | 689 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10691 | 691 | 690 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10692 | 692 | 691 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10693 | 693 | 692 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10694 | 694 | 693 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10695 | 695 | 694 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10696 | 696 | 695 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10697 | 697 | 696 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10698 | 698 | 697 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10699 | 699 | 698 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10700 | 700 | 699 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10701 | 701 | 700 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10702 | 702 | 701 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10703 | 703 | 702 | 0x02 | N
| Reserved | BOOL | 1 | 0 | 1 | 1 | 1 | R | 10704 | 704 | 703 | 0x02 | N
Note on B656: Vrund Rana: Write PubKey is applicable to Ethernet variants Internal Temperature minor error detected is not applicable to Ethernet variant

## Data Records
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Trip Record
Record 1 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46001 | 6001 | 6000 | 0x03 | Y
Record 2 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46033 | 6033 | 6032 | 0x03 | Y
Record 3 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46065 | 6065 | 6064 | 0x03 | Y
Record 4 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46097 | 6097 | 6096 | 0x03 | Y
Record 5 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46129 | 6129 | 6128 | 0x03 | Y
Record 6 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46161 | 6161 | 6160 | 0x03 | Y
Record 7 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46193 | 6193 | 6192 | 0x03 | Y
Record 8 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46225 | 6225 | 6224 | 0x03 | Y
Record 9 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46257 | 6257 | 6256 | 0x03 | Y
Record 10 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46289 | 6289 | 6288 | 0x03 | Y
Record 11 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46321 | 6321 | 6320 | 0x03 | Y
Record 12 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46353 | 6353 | 6352 | 0x03 | Y
Record 13 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46385 | 6385 | 6384 | 0x03 | Y
Record 14 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46417 | 6417 | 6416 | 0x03 | Y
Record 15 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46449 | 6449 | 6448 | 0x03 | Y
Record 16 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46481 | 6481 | 6480 | 0x03 | Y
Record 17 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46513 | 6513 | 6512 | 0x03 | Y
Record 18 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46545 | 6545 | 6544 | 0x03 | Y
Record 19 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46577 | 6577 | 6576 | 0x03 | Y
Record 20 | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | R | 46609 | 6609 | 6608 | 0x03 | Y
Event Log
Record 1 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47001 | 7001 | 7000 | 0x03 | Y
Record 2 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47009 | 7009 | 7008 | 0x03 | Y
Record 3 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47017 | 7017 | 7016 | 0x03 | Y
Record 4 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47025 | 7025 | 7024 | 0x03 | Y
Record 5 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47033 | 7033 | 7032 | 0x03 | Y
Record 6 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47041 | 7041 | 7040 | 0x03 | Y
Record 7 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47049 | 7049 | 7048 | 0x03 | Y
Record 8 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47057 | 7057 | 7056 | 0x03 | Y
Record 9 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47065 | 7065 | 7064 | 0x03 | Y
Record 10 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47073 | 7073 | 7072 | 0x03 | Y
Record 11 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47081 | 7081 | 7080 | 0x03 | Y
Record 12 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47089 | 7089 | 7088 | 0x03 | Y
Record 13 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47097 | 7097 | 7096 | 0x03 | Y
Record 14 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47105 | 7105 | 7104 | 0x03 | Y
Record 15 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47113 | 7113 | 7112 | 0x03 | Y
Record 16 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47121 | 7121 | 7120 | 0x03 | Y
Record 17 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47129 | 7129 | 7128 | 0x03 | Y
Record 18 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47137 | 7137 | 7136 | 0x03 | Y
Record 19 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47145 | 7145 | 7144 | 0x03 | Y
Record 20 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47153 | 7153 | 7152 | 0x03 | Y
Record 21 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47161 | 7161 | 7160 | 0x03 | Y
Record 22 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47169 | 7169 | 7168 | 0x03 | Y
Record 23 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47177 | 7177 | 7176 | 0x03 | Y
Record 24 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47185 | 7185 | 7184 | 0x03 | Y
Record 25 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47193 | 7193 | 7192 | 0x03 | Y
Record 26 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47201 | 7201 | 7200 | 0x03 | Y
Record 27 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47209 | 7209 | 7208 | 0x03 | Y
Record 28 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47217 | 7217 | 7216 | 0x03 | Y
Record 29 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47225 | 7225 | 7224 | 0x03 | Y
Record 30 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47233 | 7233 | 7232 | 0x03 | Y
Record 31 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47241 | 7241 | 7240 | 0x03 | Y
Record 32 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47249 | 7249 | 7248 | 0x03 | Y
Record 33 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47257 | 7257 | 7256 | 0x03 | Y
Record 34 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47265 | 7265 | 7264 | 0x03 | Y
Record 35 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47273 | 7273 | 7272 | 0x03 | Y
Record 36 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47281 | 7281 | 7280 | 0x03 | Y
Record 37 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47289 | 7289 | 7288 | 0x03 | Y
Record 38 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47297 | 7297 | 7296 | 0x03 | Y
Record 39 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47305 | 7305 | 7304 | 0x03 | Y
Record 40 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47313 | 7313 | 7312 | 0x03 | Y
Record 41 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47321 | 7321 | 7320 | 0x03 | Y
Record 42 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47329 | 7329 | 7328 | 0x03 | Y
Record 43 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47337 | 7337 | 7336 | 0x03 | Y
Record 44 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47345 | 7345 | 7344 | 0x03 | Y
Record 45 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47353 | 7353 | 7352 | 0x03 | Y
Record 46 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47361 | 7361 | 7360 | 0x03 | Y
Record 47 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47369 | 7369 | 7368 | 0x03 | Y
Record 48 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47377 | 7377 | 7376 | 0x03 | Y
Record 49 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47385 | 7385 | 7384 | 0x03 | Y
Record 50 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47393 | 7393 | 7392 | 0x03 | Y
Record 51 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47401 | 7401 | 7400 | 0x03 | Y
Record 52 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47409 | 7409 | 7408 | 0x03 | Y
Record 53 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47417 | 7417 | 7416 | 0x03 | Y
Record 54 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47425 | 7425 | 7424 | 0x03 | Y
Record 55 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47433 | 7433 | 7432 | 0x03 | Y
Record 56 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47441 | 7441 | 7440 | 0x03 | Y
Record 57 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47449 | 7449 | 7448 | 0x03 | Y
Record 58 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47457 | 7457 | 7456 | 0x03 | Y
Record 59 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47465 | 7465 | 7464 | 0x03 | Y
Record 60 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47473 | 7473 | 7472 | 0x03 | Y
Record 61 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47481 | 7481 | 7480 | 0x03 | Y
Record 62 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47489 | 7489 | 7488 | 0x03 | Y
Record 63 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47497 | 7497 | 7496 | 0x03 | Y
Record 64 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47505 | 7505 | 7504 | 0x03 | Y
Record 65 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47513 | 7513 | 7512 | 0x03 | Y
Record 66 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47521 | 7521 | 7520 | 0x03 | Y
Record 67 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47529 | 7529 | 7528 | 0x03 | Y
Record 68 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47537 | 7537 | 7536 | 0x03 | Y
Record 69 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47545 | 7545 | 7544 | 0x03 | Y
Record 70 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47553 | 7553 | 7552 | 0x03 | Y
Record 71 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47561 | 7561 | 7560 | 0x03 | Y
Record 72 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47569 | 7569 | 7568 | 0x03 | Y
Record 73 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47577 | 7577 | 7576 | 0x03 | Y
Record 74 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47585 | 7585 | 7584 | 0x03 | Y
Record 75 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47593 | 7593 | 7592 | 0x03 | Y
Record 76 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47601 | 7601 | 7600 | 0x03 | Y
Record 77 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47609 | 7609 | 7608 | 0x03 | Y
Record 78 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47617 | 7617 | 7616 | 0x03 | Y
Record 79 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47625 | 7625 | 7624 | 0x03 | Y
Record 80 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47633 | 7633 | 7632 | 0x03 | Y
Record 81 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47641 | 7641 | 7640 | 0x03 | Y
Record 82 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47649 | 7649 | 7648 | 0x03 | Y
Record 83 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47657 | 7657 | 7656 | 0x03 | Y
Record 84 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47665 | 7665 | 7664 | 0x03 | Y
Record 85 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47673 | 7673 | 7672 | 0x03 | Y
Record 86 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47681 | 7681 | 7680 | 0x03 | Y
Record 87 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47689 | 7689 | 7688 | 0x03 | Y
Record 88 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47697 | 7697 | 7696 | 0x03 | Y
Record 89 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47705 | 7705 | 7704 | 0x03 | Y
Record 90 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47713 | 7713 | 7712 | 0x03 | Y
Record 91 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47721 | 7721 | 7720 | 0x03 | Y
Record 92 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47729 | 7729 | 7728 | 0x03 | Y
Record 93 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47737 | 7737 | 7736 | 0x03 | Y
Record 94 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47745 | 7745 | 7744 | 0x03 | Y
Record 95 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47753 | 7753 | 7752 | 0x03 | Y
Record 96 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47761 | 7761 | 7760 | 0x03 | Y
Record 97 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47769 | 7769 | 7768 | 0x03 | Y
Record 98 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47777 | 7777 | 7776 | 0x03 | Y
Record 99 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47785 | 7785 | 7784 | 0x03 | Y
Record 100 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 47793 | 7793 | 7792 | 0x03 | Y
Device Internal Log
Record 1 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48001 | 8001 | 8000 | 0x03 | Y
Record 2 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48009 | 8009 | 8008 | 0x03 | Y
Record 3 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48017 | 8017 | 8016 | 0x03 | Y
Record 4 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48025 | 8025 | 8024 | 0x03 | Y
Record 5 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48033 | 8033 | 8032 | 0x03 | Y
Record 6 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48041 | 8041 | 8040 | 0x03 | Y
Record 7 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48049 | 8049 | 8048 | 0x03 | Y
Record 8 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48057 | 8057 | 8056 | 0x03 | Y
Record 9 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48065 | 8065 | 8064 | 0x03 | Y
Record 10 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48073 | 8073 | 8072 | 0x03 | Y
Record 11 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48081 | 8081 | 8080 | 0x03 | Y
Record 12 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48089 | 8089 | 8088 | 0x03 | Y
Record 13 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48097 | 8097 | 8096 | 0x03 | Y
Record 14 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48105 | 8105 | 8104 | 0x03 | Y
Record 15 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48113 | 8113 | 8112 | 0x03 | Y
Record 16 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48121 | 8121 | 8120 | 0x03 | Y
Record 17 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48129 | 8129 | 8128 | 0x03 | Y
Record 18 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48137 | 8137 | 8136 | 0x03 | Y
Record 19 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48145 | 8145 | 8144 | 0x03 | Y
Record 20 | UINT16 | 16 | 8 | 0 | 65535 | 1 | 1 | R | 48153 | 8153 | 8152 | 0x03 | Y
Motor Start - Latest Log
Record 1 | UINT16 | 512 | 256 | 0 | 65535 | 1 | 1 | R | 48376 | 8376 | 8375 | 0x03 | Y
Motor Start - Reference Log
Record 1 | UINT16 | 512 | 256 | 0 | 65535 | 1 | 1 | R | 48751 | 8751 | 8750 | 0x03 | Y
Audit Log
Query |  | Slave Address | Function Code:0x47 | Record Number (Max. value:2048) | Number Of Records to read (Max. Value: 12) | CRC
Size in Byte |  | 1 | 1 | 2 | 2 | 2
Response |  | Slave Address | Function Code:0x47 | Record Number (Max. value:2048) | Number Of Records to read (Max. Value: 12) | Record 1 | Record 2 | …............... | Record 12 |  |  | CRC
Size in Byte |  | 1 | 1 | 2 | 2 | 20 | 20 |  | 20 |  |  | 2
Exceprion response |  | Slave Address | Function Code:0xC7 | Error Code | CRC
Size in Byte |  | 1 | 1 | 2 | 2
Audit Record |  | Parameters | Parameter Size in Bytes | Record Size in Bytes
Record 1 |  | Event Identifier | 4 | 20
|  | Timestamp | 8
|  | Source | 2
|  | Category | 2
|  | Event Type | 2
|  | Event Result | 2
Record 2 |  | Event Identifier | 4 | 20
|  | Timestamp | 8
|  | Source | 2
|  | Category | 2
|  | Event Type | 2
|  | Event Result | 2
.
.
.
Record 12 |  | Event Identifier | 4 | 20
|  | Timestamp | 8
|  | Source | 2
|  | Category | 2
|  | Event Type | 2
|  | Event Result | 2
|  |  | Total size in Bytes | 240

## Product Info
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Product Information
Product ID | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49126 | 9126 | 9125 | 0x03 | Y
Product S/R Number | ASCII | 32 | 16 | 0 | 4294967295 | 1 | 1 | R | 49128 | 9128 | 9127 | 0x03 | Y |  |  | Product S/R number is in ASCII format
Manufacture Day | UINT16 | 2 | 1 | 1 | 31 | 1 | 1 | R | 49144 | 9144 | 9143 | 0x03 | Y
Manufacture Month | UINT16 | 2 | 1 | 1 | 12 | 1 | 1 | R | 49145 | 9145 | 9144 | 0x03 | Y
Manufacture Year | UINT16 | 2 | 1 | 2017 | 2999 | 1 | 1 | R | 49146 | 9146 | 9145 | 0x03 | Y
Manufacture Hour | UINT16 | 2 | 1 | 0 | 23 | 1 | 1 | R | 49147 | 9147 | 9146 | 0x03 | Y
Manufacture Min | UINT16 | 2 | 1 | 0 | 59 | 1 | 1 | R | 49148 | 9148 | 9147 | 0x03 | Y
Manufacture Seconds | UINT16 | 2 | 1 | 0 | 59 | 1 | 1 | R | 49149 | 9149 | 9148 | 0x03 | Y
Standard Package Version | UINT16 | 4 | 2 | 0 | 65535 | 1 | 1 | R | 49150 | 9150 | 9149 | 0x03 | Y
Reserved | UINT16 | 2 | 1 | 0 | 0 | 0 | 0 | R | 49152 | 9152 | 9151 | 0x03 | N
Product Order code | ASCII | 20 | 10 | 0 | 4294967295 | 1 | 1 | R | 49153 | 9153 | 9152 | 0x03 | Y |  |  | Product code is currently unused
Main Unit Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49163 | 9163 | 9162 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49165 | 9165 | 9164 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49167 | 9167 | 9166 | 0x03 | Y
CTVT Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49169 | 9169 | 9168 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49171 | 9171 | 9170 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49173 | 9173 | 9172 | 0x03 | Y
Display Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49175 | 9175 | 9174 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49177 | 9177 | 9176 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49179 | 9179 | 9178 | 0x03 | Y
EXP1 Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49181 | 9181 | 9180 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49183 | 9183 | 9182 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49185 | 9185 | 9184 | 0x03 | Y
EXP2 Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49187 | 9187 | 9186 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49189 | 9189 | 9188 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49191 | 9191 | 9190 | 0x03 | Y
EXP3 Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49193 | 9193 | 9192 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49195 | 9195 | 9194 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49197 | 9197 | 9196 | 0x03 | Y
EXP4 Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49199 | 9199 | 9198 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49201 | 9201 | 9200 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49203 | 9203 | 9202 | 0x03 | Y
EXP5 Version
Hardware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49205 | 9205 | 9204 | 0x03 | Y |  |  | ASCII format
Firmware Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49207 | 9207 | 9206 | 0x03 | Y
Boot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49209 | 9209 | 9208 | 0x03 | Y
MAC ADDRESS
MAC ADDRESS 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | R | 49211 | 9211 | 9210 | 0x03 | Y
MAC ADDRESS 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | R | 49212 | 9212 | 9211 | 0x03 | Y
MAC ADDRESS 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | R | 49213 | 9213 | 9212 | 0x03 | Y
MAC ADDRESS 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | R | 49214 | 9214 | 9213 | 0x03 | Y
MAC ADDRESS 4 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | R | 49215 | 9215 | 9214 | 0x03 | Y
MAC ADDRESS 5 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | R | 49216 | 9216 | 9215 | 0x03 | Y
Detected Expansions
Sensor Module Type | UINT16 | 2 | 1 | 0 | 17 | 1 | 1 | R | 49217 | 9217 | 9216 | 0x03 | N |  |  | 1 - LTMTCT3L 2 - LTMTCTV3L 3 - LTMTCT3T 4 - LTMTCTV3T 5 - LTMTCT25L 6 - LTMTCTV25L 7 - LTMTCT25T 8 - LTMTCTV25T 9 - LTMTCT100L 10 - LTMTCTV100L 11 - LTMTCT100T 12 - LTMTCTV100T 13 - LTMTCT70L 14 - LTMTCTV70L 15 - LTMTCTV3UT 16 - LTMTCTV25UT 17 - LTMTCTV100UT
| UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | R | 49218 | 9218 | 9217 | 0x03 | N
Expansion Module 1 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | R | 49219 | 9219 | 9218 | 0x03 | N |  |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 2 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | R | 49220 | 9220 | 9219 | 0x03 | N |  |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 3 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | R | 49221 | 9221 | 9220 | 0x03 | N |  |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 4 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | R | 49222 | 9222 | 9221 | 0x03 | N |  |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
Expansion Module 5 Type | UINT16 | 2 | 1 | 0 | 8 | 1 | 1 | R | 49223 | 9223 | 9222 | 0x03 | N |  |  | 0 - None 1 - LTMTIN42FM 2 - LTMTIN42BD 3 - LTMTIN60FM 4 - LTMTIN60BD 5 - LTMTZCT22FM 6 - LTMTZCT22BD 7 - LTMTAN21 8 - LTMTPTC
EIP Product Details
Vendor ID | UINT16 | 2 | 1 | 243 | 243 | NA | NA | R | 49224 | 9224 | 9223 | 0x03 | N |  |  | 49 | 31 | 243
Device Profile | UINT16 | 2 | 1 | 22 | 22 | NA | NA | R | 49225 | 9225 | 9224 | 0x03 | N |  |  | 50 | 32 | 22
Product Code | UINT16 | 4 | 2 | See Remark |  | NA | NA | R | 49226 | 9226 | 9225 | 0x03 | N |  |  | 51 | 33 | 240VAC= 0x3401 ; 24VDC = 0x3402
CIP Serial Number | UINT16 | 4 | 2 | See Remark |  | NA | NA | R | 49228 | 9228 | 9227 | 0x03 | N |  |  | 52 | 34 | Third Last byte of MAC: second last byte of Mac: Last byte of MAC : 0x20(0x20 is for Tesys T: will get for tera after registering our device with ODVA)
Version (Internal Only)
Uboot Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49230 | 9230 | 9229 | 0x03 | Y |  |  | ASCII format
Kernel Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49232 | 9232 | 9231 | 0x03 | Y
Filesystem Version | UINT32 | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 49234 | 9234 | 9233 | 0x03 | Y
Note on B5: Product S/R number is in ASCII format
Note on B12: Byte info: MSB 0,1:Patch Version 2: Major version LSB 3: Minor version
Note on B17: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B18: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B21: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B22: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B25: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B26: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B29: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B30: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B33: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B34: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B37: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B38: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B41: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B42: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B45: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version
Note on B46: Byte info: MSB 0: Reserved 1: Reserved 2: Major version LSB 3: Minor version

## Product Info - Extended
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
CTVT Serial Number
Serial Number | UINT16 | 20 | 10 | 0 | 65535 | 1 | 1 | R | 43251 | 3251 | 3250 | 0x03 | N
EXP1 Serial Number
Serial Number | UINT16 | 20 | 10 | 0 | 65535 | 1 | 1 | R | 43261 | 3261 | 3260 | 0x03 | N
EXP2 Serial Number
Serial Number | UINT16 | 20 | 10 | 0 | 65535 | 1 | 1 | R | 43271 | 3271 | 3270 | 0x03 | N
N
Serial Number | UINT16 | 20 | 10 | 0 | 65535 | 1 | 1 | R | 43281 | 3281 | 3280 | 0x03 | N
EXP4 Serial Number
Serial Number | UINT16 | 20 | 10 | 0 | 65535 | 1 | 1 | R | 43291 | 3291 | 3290 | 0x03 | N
EXP5 Serial Number
Serial Number | UINT16 | 20 | 10 | 0 | 65535 | 1 | 1 | R | 43301 | 3301 | 3300 | 0x03 | N
Main Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43376 | 3376 | 3375 | 0x03, 0x06, 0x10 | Y
CTVT Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43381 | 3381 | 3380 | 0x03, 0x06, 0x10 | Y
EXP1 Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43386 | 3386 | 3385 | 0x03, 0x06, 0x10 | Y
EXP2 Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43391 | 3391 | 3390 | 0x03, 0x06, 0x10 | Y
EXP3 Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43396 | 3396 | 3395 | 0x03, 0x06, 0x10 | Y
EXP4 Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43401 | 3401 | 3400 | 0x03, 0x06, 0x10 | Y
EXP5 Module Tag
Serial Number | UINT16 | 10 | 5 | 0 | 65535 | 1 | 1 | RW | 43406 | 3406 | 3405 | 0x03, 0x06, 0x10 | Y

## Device Identification
FC43 - Device identification
| Object ID | Object Name | Type | M/O | Assignment | Category | Size(Bytes)
| 0 | Vender Name | ASCII String | Mandatory | "Schneider Electric" (configurable) | Basic | 20
| 1 | Product Code | ASCII String | Mandatory | TBD (configurable) |  | 20
| 2 | Major Minor Revision | ASCII String | Mandatory | TBD (configurable) |  | 10
| 3 | Vendor URL | ASCII String | Optional | www.se.com (configurable) | Reguler | 20
| 4 | Product name | ASCII String | Optional | Motor protection relay (configurable) |  | 26
| 5 | Model Name | ASCII String | Optional | Tesys Tera (configurable) |  | 10
| 6 | User Application Name | ASCII String | Optional | TBD (configurable) |  | 32
FC66 User Define query
Device ID | FC | length | Data | CRC
1 | 66 | 186
| Data | Parameter | size
|  | Sr .No | 32
|  | Day | 2
|  | Month | 2
|  | Year | 2
|  | HR | 2
|  | MIN | 2
|  | SEC | 2
|  | HW VERSION | 4
|  | Product Code | 20
|  | Vender Name | 20
|  | Major Minor Revision | 10
|  | Vendor URL | 20
|  | Product name | 26
|  | Model Name | 10
|  | User Application Name | 32

## Internal Data
Attribute Name | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Function Codes | Default Value | Units | Remarks
Read Only Data
Display Status Data
Thermal Memory | 2 | 1 | 0 | 100 | 1 | 1 | R | 34876 | 0x04 |  | %
Full load Current | 2 | 1 | 3 | 50000 | 1 | 1/10 | R | 34877 | 0x04 |  | Amp
Motor Info | 4 | 2 | 1 | 4294967295 | 1 | 1 | R | 34878 | 0x04
Trip Code | 2 | 1 | 1 | 65535 | 1 | 1 | R | 34880 | 0x04
Display PowerUp Data
Motor Tag | 30 | 15 | 0 | 65535 | 1 | 1 | R | 34881 | 0x04
Number of expansion unit | 2 | 1 | 0 | 5 | 1 | 1 | R | 34896 | 0x04
Expansion Module 1 Type | 2 | 1 | 0 | 4 | 1 | 1 | R | 34897 | 0x04
Expansion Module 2 Type | 2 | 1 | 0 | 4 | 1 | 1 | R | 34898 | 0x04
Expansion Module 3 Type | 2 | 1 | 0 | 4 | 1 | 1 | R | 34899 | 0x04
Expansion Module 4 Type | 2 | 1 | 0 | 4 | 522147 | 1 | R | 34900 | 0x04
Expansion Module 5 Type | 2 | 1 | 0 | 4 | 1 | 1 | R | 34901 | 0x04
Expansion Module 1 Variant | 2 | 1 | 0 | 10 | 1 | 1 | R | 34902 | 0x04
Expansion Module 2 Variant | 2 | 1 | 0 | 10 | 1 | 1 | R | 34903 | 0x04
Expansion Module 3 Variant | 2 | 1 | 0 | 10 | 1 | 1 | R | 34904 | 0x04
Expansion Module 4 Variant | 2 | 1 | 0 | 10 | 1 | 1 | R | 34905 | 0x04
Expansion Module 5 Variant | 2 | 1 | 0 | 10 | 1 | 1 | R | 34906 | 0x04
CT type | 2 | 1 | 0 | 5 | 1 | 1 | R | 34907 | 0x04
Logic ID | 2 | 1 | 0 | 512 | 1 | 1 | R | 34908 | 0x04
Main unit- Communication type | 2 | 1 | 0 | 6 | 1 | 1 | R | 34909 | 0x04
Starter Type (EOM ID) | 2 | 1 | 0 | 15 | 1 | 1 | R | 34910 | 0x04
Test Mode (Enable/Disable) | 2 | 1 | 0 | 1 | 1 | 1 | R | 34911 | 0x04
Main Unit Temp | 2 | 1 | 0 | 2 | 1 | 1 | R | 34912 | 0x04
Load Type | 2 | 1 | 0 | 1 | 1 | 1 | R | 34913 | 0x04
Emergency Start | 2 | 1 | 0 | 1 | 1 | 1 | R | 34914 | 0x04
Max Start Function | 2 | 1 | 0 | 1 | 1 | 1 | R | 34915 | 0x04
Debug counters
Main unit to CTVT Query Counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34501 | 0x04
Main unit to Exp Query Counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34503 | 0x04
Main unit CTVT valid response counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34505 | 0x04
Main unit Exp1 valid response counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34507 | 0x04
Main unit Exp2 valid response counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34509 | 0x04
Main unit Exp3 valid response counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34511 | 0x04
Main unit Exp4 valid response counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34513 | 0x04
Main unit Exp5 valid response counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34515 | 0x04
Main unit to CTVT Comm Fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34517 | 0x04
Main unit to EXP1 Comm Fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34519 | 0x04
Main unit to EXP2 Comm Fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34521 | 0x04
Main unit to EXP3 Comm Fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34523 | 0x04
Main unit to EXP4 Comm Fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34525 | 0x04
Main unit to EXP5 Comm Fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34527 | 0x04
EEPROM Write fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34529 | 0x04
EEPROM read fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34531 | 0x04
EEPROM Write cycle counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34533 | 0x04
Internal temperature fault counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34535 | 0x04
PROFIBUS communication fail counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34537 | 0x04
Modbus communication timeout counter | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 34539 | 0x04
Internal temperature max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34541 | 0x04
Main unit to CTVT Comm retry counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34542 | 0x04
Main unit to EXP Comm retry counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34543 | 0x04
HMI comunication timeout counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34544 | 0x04
EEPROM Checksum fail counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34545 | 0x04
Stack Usage of Protection task | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34546 | 0x04
Stack Usage of Communication task | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34547 | 0x04
Stack Usage of CTVT task | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34548 | 0x04
Stack Usage of Exp task | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34549 | 0x04
Stack Usage of DISP task | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34550 | 0x04
Stack usage of NVModule task | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34551 | 0x04
Reoccurance time of Protection task max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34552 | 0x04
Reoccurance time of Communication task max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34553 | 0x04
Reoccurance time of CTVT task max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34554 | 0x04
Reoccurance time of Exp task max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34555 | 0x04
Reoccurance time of DISP task max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34556 | 0x04
Reoccurance time of NVModule task max | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34557 | 0x04
Average Queries per seconds to CTVT | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34558 | 0x04
Average Queries per seconds to Exp | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34559 | 0x04
max Queries per seconds to CTVT | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34560 | 0x04
max Queries per seconds to Exp | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34561 | 0x04
Power Down detection counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34562 | 0x04
Power Down counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34563 | 0x04
Power Up counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34564 | 0x04
Watchdog reset counter | 2 | 1 | 0 | 65535 | 1 | 1 | R | 34565 | 0x04
Read Write Data
Motor Validation Time
Motor Stop Validation Time | 2 | 1 | 0 | 40000 | 5 | 1 | RW | 49251 | 0x03,0x06,0x10
Motor Start Validation Time | 2 | 1 | 0 | 40000 | 5 | 1 | RW | 49252 | 0x03,0x06,0x10
Motor Run Validation Time | 2 | 1 | 0 | 40000 | 5 | 1 | RW | 49253 | 0x03,0x06,0x10
Older CTVT Version | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49254 | 0x03,0x06,0x10
Motor RUN Threshold | 2 | 1 | 50 | 300 | 1 | 1 | RW | 49255 | 0x03,0x06,0x10
Version Support | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49256 | 0x03,0x06,0x10
Force start command time | 2 | 1 | 0 | 60000 | 1 | 1 | RW | 49257 | 0x03,0x06,0x10
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49258 | 0x03,0x06,0x10
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49259 | 0x03,0x06,0x10
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49260 | 0x03,0x06,0x10
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49261 | 0x03,0x06,0x10
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49262 | 0x03,0x06,0x10
Display Version Info
Hardware Version | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49263 | 0x03,0x06,0x10
Software Version | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49265 | 0x03,0x06,0x10
Boot Software Version | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49267 | 0x03,0x06,0x10
Main Unit Temperature Calibration Factor
RTD Calibration Slope | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 49269 | 0x03,0x06,0x10
RTD Calibration Constant | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 49270 | 0x03,0x06,0x10
PTC Calibration Slope | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 49271 | 0x03,0x06,0x10
Calibration Day | 2 | 1 | 1 | 31 | 1 | 1 | RW | 49272 | 0x03,0x06,0x10
Calibration Month | 2 | 1 | 1 | 12 | 1 | 1 | RW | 49273 | 0x03,0x06,0x10
Calibration Year | 2 | 1 | 2000 | 2999 | 1 | 1 | RW | 49274 | 0x03,0x06,0x10
Calibration Hours | 2 | 1 | 0 | 23 | 1 | 1 | RW | 49275 | 0x03,0x06,0x10
Calibration Minutes | 2 | 1 | 0 | 59 | 1 | 1 | RW | 49276 | 0x03,0x06,0x10
Calibration Seconds | 2 | 1 | 0 | 59 | 1 | 1 | RW | 49277 | 0x03,0x06,0x10
PTC Calibration constant | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 49278 | 0x03,0x06,0x10
RTD/PTC Resistance | 2 | 1 | 0 | 0 | 0 | 0 | R | 49279 | 0x03
RTD/PTC Voltage | 2 | 1 | 0 | 0 | 0 | 0 | R | 49280 | 0x03
CTVT Calibration Factors
R Phase Voltage | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49281 | 0x03,0x06,0x10
Y Phase Voltage | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49283 | 0x03,0x06,0x10
B Phase Voltage | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49285 | 0x03,0x06,0x10
R Phase Current High Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49287 | 0x03,0x06,0x10
R Phase Current Low Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49289 | 0x03,0x06,0x10
Y Phase Current High Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49291 | 0x03,0x06,0x10
Y Phase Current Low Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49293 | 0x03,0x06,0x10
B Phase Current High Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49295 | 0x03,0x06,0x10
B Phase Current Low Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49297 | 0x03,0x06,0x10
R Phase Power High Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49299 | 0x03,0x06,0x10
R Phase Power Low Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49301 | 0x03,0x06,0x10
Y Phase Power High Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49303 | 0x03,0x06,0x10
Y Phase PowerLow Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49305 | 0x03,0x06,0x10
B Phase Power High Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49307 | 0x03,0x06,0x10
B Phase Power Low Gain | 4 | 2 | 0 | 4294967295 | 1 | 1 | RW | 49309 | 0x03,0x06,0x10
Calibration Day | 2 | 1 | 1 | 31 | 1 | 1 | RW | 49311 | 0x03,0x06,0x10
Calibration Month | 2 | 1 | 1 | 12 | 1 | 1 | RW | 49312 | 0x03,0x06,0x10
Calibration Year | 2 | 1 | 2000 | 2999 | 1 | 1 | RW | 49313 | 0x03,0x06,0x10
Calibration Hours | 2 | 1 | 0 | 23 | 1 | 1 | RW | 49314 | 0x03,0x06,0x10
Calibration Minutes | 2 | 1 | 0 | 59 | 1 | 1 | RW | 49315 | 0x03,0x06,0x10
Calibration Seconds | 2 | 1 | 0 | 59 | 1 | 1 | RW | 49316 | 0x03,0x06,0x10
Main unit Card Level Test
Key Status | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49317 | 0x03
LED | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 49318 | 0x03,0x06,0x10
Main unit RTC Calibration
CALM | 2 | 1 | 0 | 511 | 1 | 1 | RW | 49319 | 0x03,0x06,0x10 | 0
CALP | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49320 | 0x03,0x06,0x10 | 0
Enable Calibration | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49321 | 0x03,0x06,0x10 | 0 |  | 0: Disable 1: Enable
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49322 | 0x03,0x06,0x10 | 0
Debug
Write Debug Counters | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49323 | 0x03,0x06,0x10 | 0
Reset debug counters | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49324 | 0x03,0x06,0x10 | 0
Main unit Manufacturing
Test Mode | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49325 | 0x03,0x06,0x10 | 0 |  | 0: Disable 1: Enable
Current Value | 2 | 1 | 0 | 600 | 1 | 1 | RW | 49326 | 0x03,0x06,0x10 | 0 |  | %IFLC
Reserved | 1098 | 549 | 0 | 0 | 0 | 0 | RW | 49327 | 0x03,0x06,0x10 | 0
MAC address for Write
Port 1
MAC byte 1 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49328 | 0x03,0x06,0x10 | schnier provided |  | eth0
MAC byte 2 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49329 | 0x03,0x06,0x10 | schnier provided
MAC byte 3 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49330 | 0x03,0x06,0x10 | schnier provided
MAC byte 4 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49331 | 0x03,0x06,0x10 | schnier provided
MAC byte 5 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49332 | 0x03,0x06,0x10 | schnier provided
MAC byte 6 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49333 | 0x03,0x06,0x10 | schnier provided
Port 2
MAC byte 1 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49334 | 0x03,0x06,0x10 | schnier provided |  | eth1 :port2 of MAC1 = MAC1 of Port1 + 1
MAC byte 2 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49335 | 0x03,0x06,0x10 | schnier provided
MAC byte 3 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49336 | 0x03,0x06,0x10 | schnier provided
MAC byte 4 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49337 | 0x03,0x06,0x10 | schnier provided
MAC byte 5 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49338 | 0x03,0x06,0x10 | schnier provided
MAC byte 6 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49339 | 0x03,0x06,0x10 | schnier provided
PDD test byte
PPDTestByte | 2 | 1 | 0 | 255 | 1 | 1 | RW | 49340 | 0x03,0x06,0x10 |  |  | Value after power up should be what is set in Power down
HMI Commands
Commands Register 1 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 49876 | 0x03,0x06,0x10 | 0 |  | bit 0: Motor run forward / High speed forward command bit 1: Motor run reverse / High speed reverse command bit 2:Local/Remote Mode Sel 1 bit 3: Trip reset command bit 4: Local/Remote Mode Sel 2 bit 5: Self test (without trip) command bit 6: Motor low speed forward command bit 7: Motor low speed reverse command bit 8: Reset Inhibit command bit 9: Reset no of starts command bit 10: Reset no of stops command bit 11: Clear Energy command bit 12: Motor Stop bit 13: Logic test command bit 14: Reset run hour command bit 15: Self test (with trip) command
Commands Register 2 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49877 | 0x03,0x06,0x10 | 0 |  | bit 0: Clear all command bit 1: Clear statistics command bit 2: Clear thermal capacity level command bit 3: Clear controller settings command bit 4: Clear network port settings command bit 5: Clear Trip counter command bit 6: Factory reset command bit 7: Soft starter reset command bits 8-12: Reserved bit 13: Store reference start curve command bit 14: Clear trip records command bit 15: Clear event records command
Internal Commands | 2 | 1 | 0 | 1 | 1 | 1 | RW | 49878 | 0x03,0x06,0x10 | 0 |  | bit 0: HMI FDR bit 1: Ethernet Global Statistic Reset bit 2: Modbus TCP port reset bit 3: General Counter Reset bit 4: Configured and learned reset bit 5: RSTP port 1 Reset bit 6: RSTP port 2 Reset
Reserved | 2 | 1 | 0 | 0 | 0 | 0 | RW | 49879 | 0x03,0x06,0x10 | 0
Firmware Update Status and Commands
Firmware Update status | 2 | 1 | 0 | 0 | 1 | 1 | R | 49880 | 0x03 |  |  | Bit 0:Main Module Firmware Available Bit 1: sensor Module Firmware Available Bit 2: Expansion Module Firmware Available Bit 3: sensor Module Firmware Update Ongoing Bit 4: Expansion Module Firmware Update Ongoing Bit 5: Main Module Firmware update Successful Bit 6: sensor Module Firmware Update Successful Bit 7: Expansion Module Firmware Update Successful
Firmware Update Command | 2 | 1 | 0 | 7 | 1 | 1 | RW | 49881 | 0x03,0x06,0x10 |  |  | Bit 0: Update Main Module Firmware Bit 1: Update Sensor Module Firmware Bit 2: Update Expansion Module Firmware
Firmware Update Error | 2 | 1 | 0 | 0 | 1 | 1 | R | 49882 | 0x03 |  |  | Bit 0: Main Module Firmware update error Bit 1: sensor Module Firmware Update error Bit 2: Expansion Module Firmware Update error Bit 3: Reserved Bit 4: Reserved Bit 5: Reserved Bit 6: Reserved Bit 7: Main Module Firmware authentication error Bit 8: sensor Module Firmware authentication error Bit 9: Expansion Module Firmware authentication error
Note on B7: Motor Info Bit Position: Word 1: 34879 1-0: Motor Status 00:Motor Stop 01:Motor Start 10:Motor Run 11:Motor Inhibit 2:Pickup 3:Alarm 4:Trip 5:Profi/Modbus Comm Fail 6:Profi/Modbus comm established 7:CTVT/Exp Comm Fail 8:IRF 9:Power ON 11-10:STARTER MODE INFO 0 0 : L1 0 1 : L2 1 0 : L3 1 1 : REMOTE 13-12: Programmable LED Indication 0 0 : OFF 0 1 : ON 1 0 : FALSHING 1 1 : FLICKERING 15-14: Test Mode 00:Reset 01:Self Test Mode 10:Logic Test Mode 11: Reserved Word 0: 34878 3-2-1-0: Motor Indicators 0001:Motor Fwd Running 0010:Motor Rev Running 0011:Motor Fast Fwd Running 0100:Motor Fast Rev Running 0101:Motor in Changeover 0110:Motor Fwd Star Running 0111:Motor Fwd Delta Running 1000:Motor Rev Star Running 1001:Motor Rev Delta Running 4:Low Battery 5: Read Power ON Data 6: Factory Reset(HMI Reset Pin) 7: User Programmable Keys (HMI Keys)
Note on B12: 0 - None 1 - 4DI2DO 2 - 6DI 3 - AIO 4 - RTD 5 - Earth Fault
Note on B13: 0 - None 1 - 4DI2DO 2 - 6DI 3 - AIO 4 - RTD 5 - Earth Fault
Note on B14: 0 - None 1 - 4DI2DO 2 - 6DI 3 - AIO 4 - RTD 5 - Earth Fault
Note on B15: 0 - None 1 - 4DI2DO 2 - 6DI 3 - AIO 4 - RTD 5 - Earth Fault
Note on B16: 0 - None 1 - 4DI2DO 2 - 6DI 3 - AIO 4 - RTD 5 - Earth Fault
Note on B22: 0 - 0.3 to 3A 1 - 2.5 to 25A 2 - 10 to 100A 3 - 20 to 200A 4 - 20 to 200A Bus Conn. 5 - 63 to 630A Bus Conn.
Note on B24: 0: None 1:Profibus 2:Modbus RTU 3:Modbus TCP 4:Profinet 5:Devicenet 6:Ethernet IP
Note on B133: 0x0000: Card Level test Disable 0x0001: LED1 OFF 0x0002: LED2 OFF 0x0003: LED3 OFF 0x0004: LED4 OFF 0x0005: LED5 OFF 0x0006: LED6 OFF 0x0007: LED7 OFF 0x0101: LED1 ON 0x0102: LED2 ON 0x0103: LED3 ON 0x0104: LED4 ON 0x0105: LED5 ON 0x0106: LED6 ON 0x0107: LED7 ON

## User defined Map
Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | Remarks
Status Word 1 Configuration
Bit 0 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49751 | 9751 | 9750 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 1 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49752 | 9752 | 9751 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 2 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49753 | 9753 | 9752 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 3 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49754 | 9754 | 9753 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 4 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49755 | 9755 | 9754 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 5 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49756 | 9756 | 9755 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 6 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49757 | 9757 | 9756 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 7 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49758 | 9758 | 9757 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 8 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49759 | 9759 | 9758 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 9 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49760 | 9760 | 9759 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 10 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49761 | 9761 | 9760 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 11 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49762 | 9762 | 9761 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 12 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49763 | 9763 | 9762 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 13 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49764 | 9764 | 9763 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 14 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49765 | 9765 | 9764 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 15 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49766 | 9766 | 9765 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Status Word 2 Configuration
Bit 0 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49767 | 9767 | 9766 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 1 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49768 | 9768 | 9767 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 2 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49769 | 9769 | 9768 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 3 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49770 | 9770 | 9769 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 4 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49771 | 9771 | 9770 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 5 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49772 | 9772 | 9771 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 6 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49773 | 9773 | 9772 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 7 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49774 | 9774 | 9773 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 8 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49775 | 9775 | 9774 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 9 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49776 | 9776 | 9775 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 10 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49777 | 9777 | 9776 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 11 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49778 | 9778 | 9777 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 12 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49779 | 9779 | 9778 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 13 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49780 | 9780 | 9779 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 14 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49781 | 9781 | 9780 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet
Bit 15 | UINT16 | 2 | 1 | 0 | 704 | 1 | 1 | RW | 49782 | 9782 | 9781 | 0x03,0x06,0x10 | Y | 0 |  | 0: None 1-704: Selectable register from 'Status' sheet

## Commercial reference
Sl. No. | Commercial Ref ID | Short Description | ERP-Print Medium Description | Type | New | US
1 | LTMTPBD | Electro relay main Profibus DP 24VDC | Electronic motor relay main unit Profibus DP 24VDC | Main Unit | New | Yes
2 | LTMTPFM | Electro relay mainProfibus DP 265V | Electronic motor relay main unit Profibus DP 265V | Main Unit | New | Yes
3 | LTMTMBD | Electro relay main Modbus 24VDC | Electronic motor relay main unit Modbus 24VDC | Main Unit | New | Yes
4 | LTMTMFM | Electro relay main Modbus 265V | Electronic motor relay main unit Modbus 265V | Main Unit | New | Yes
5 | LTMTEBD | Electro relay main EtherNet TCP/IP 24VDC | Electronic motor relay main unit EtherNet TCP/IP 24VDC | Main Unit | New | Yes
6 | LTMTEFM | Electro relay main EtherNet TCP/IP 265V | Electronic motor relay main unit EtherNet TCP/IP 265V | Main Unit | New | Yes
7 | LTMTPNBD | Electro relay main ProfiNet 24VDC | Electronic motor relay main unit ProfiNet 24VDC | Main Unit | New | Yes
8 | LTMTPNFM | Electro relay main ProfiNet 265V | Electronic motor relay main unit ProfiNet 265V | Main Unit | New | Yes
9 | LTMT618BD | Electro relay main IEC 61850 24VDC | Electronic motor relay main unit IEC 61850 24VDC | Main Unit | New | NA
10 | LTMT618FM | Electro relay main IEC 61850 265V | Electronic motor relay main unit IEC 61850 265V | Main Unit | New | NA
11 | LTMTCT3L | Electro relay sensor CT 0.3-3A | Electronic motor relay sensor CT 0.3-3A | Sensor | New | NA
12 | LTMTCT25L | Electro relay sensor CT 2.5-25A | Electronic motor relay sensor CT 2.5-25A | Sensor | New | NA
13 | LTMTCT70L | Electro relay sensor CT 7-70A | Electronic motor relay sensor CT 7-70A | Sensor | New | NA
14 | LTMTCT100L | Electro relay sensor CT 10-100A | Electronic motor relay sensor CT 10-100A | Sensor | New | NA
15 | LTMTCT3T | Electro relay sensor CT Horizontal 0.3-3A | Electronic motor relay sensor CT Horizontal 0.3-3A | Sensor | New | NA
16 | LTMTCT25T | Electro relay sensor CT Horizontal 2.5-25A | Electronic motor relay sensor CT Horizontal 2.5-25A | Sensor | New | NA
17 | LTMTCT100T | Electro relay sensor CT Horizontal 10-100A | Electronic motor relay sensor CT Horizontal 10-100A | Sensor | New | NA
18 | LTMTCTV3L | Electro relay sensor CTVT 0.3-3A | Electronic motor relay sensor CTVT 0.3-3A | Sensor | New | NA
19 | LTMTCTV25L | Electro relay sensor CTVT 2.5-25A | Electronic motor relay sensor CTVT 2.5-25A | Sensor | New | NA
20 | LTMTCTV70L | Electro relay sensor CTVT 7-70A | Electronic motor relay sensor CTVT 7-70A | Sensor | New | NA
21 | LTMTCTV100L | Electro relay sensor CTVT 10-100A | Electronic motor relay sensor CTVT 10-100A | Sensor | New | NA
22 | LTMTCTV3T | Electro relay sensor CTVT Horizont 0.3-3A | Electronic motor relay sensor CTVT Horizontal 0.3-3A | Sensor | New | NA
23 | LTMTCTV25T | Electro relay sensor CTVT Horizont 2.5-25A | Electronic motor relay sensor CTVT Horizontal 2.5-25A | Sensor | New | NA
24 | LTMTCTV100T | Electro relay sensor CTVT Horizont 10-100A | Electronic motor relay sensor CTVT Horizontal 10-100A | Sensor | New | NA
25 | LTMTIN42FM | Electro relay exp 4 DI + 2 DO AC | Electronic motor relay expansion Digital 4 Inputs 2 Outputs AC | Expansion Module | New | Yes
26 | LTMTIN42BD | Electro relay exp 4 DI + 2 DO DC | Electronic motor relay expansion Digital 4 Inputs 2 Outputs DC | Expansion Module | New | Yes
27 | LTMTIN60FM | Electro relay exp 6 DI AC | Electronic motor relay expansion 6 Digital Inputs AC | Expansion Module | New | Yes
28 | LTMTIN60BD | Electro relay exp 6 DI DC | Electronic motor relay expansion 6 Digital Inputs DC | Expansion Module | New | Yes
29 | LTMTZCT22FM | Electro relay exp Earth Fault AC | Electronic motor relay expansion Earth Fault AC | Expansion Module | New | Yes
30 | LTMTZCT22BD | Electro relay exp Earth Fault DC | Electronic motor relay expansion Earth Fault DC | Expansion Module | New | Yes
31 | LTMTAN21 | Electro relay exp Analog | Electronic motor relay expansion Analog | Expansion Module | New | Yes
32 | LTMTPTC | Electro relay exp Additional PTC | Electronic motor relay expansion Additional PTC | Expansion Module | New | Yes
33 | LTMT9TCS | Electro relay spare connector screw | Electronic motor relay spare connector screw | Screw | New | Yes
34 | LTMT9TCP | Electro relay spare connector pushin | Electronic motor relay spare connector pushin | Pushin connector | New | Yes
35 | LTMT9RJ105 | Electro relay main CT RJ11 CONNECT 0,5M | Electronic motor relay main to Sensor RJ11 CONNECTOR 0,5M | Cable - Sensor | New | Yes
36 | LTMT9RJ1015 | Electro relay main CT RJ11 CONNECT 0,15M | Electronic motor relay main to sensor RJ11 CONNECTOR 0,15M | Cable - Sensor | New | Yes
37 | LTMT9RJ401 | Electro relay exp CT RJ45 CONNECT 0,1M | Electronic motor relay expansion cable RJ45 CONNECTOR 0,1M | Cable - Expansion | New | Yes
38 | LTMTCT3UT | Electro relay sensor CT Horizontal 0.3-3A US | Electronic motor relay sensor CT Horizontal 0.3-3A US | Sensor | New | Yes
39 | LTMTCT25UT | Electro relay sensor CT Horizontal 2.5-25A US | Electronic motor relay sensor CT Horizontal 2.5-25A US | Sensor | New | Yes
40 | LTMTCT100UT | Electro relay sensor CT Horizontal 10-100A US | Electronic motor relay sensor CT Horizontal 10-100A US | Sensor | New | Yes
41 | LTMTCTV3UT | Electro relay sensor CTVT Horizont 0.3-3A US | Electronic motor relay sensor CTVT Horizontal 0.3-3A US | Sensor | New | Yes
42 | LTMTCTV25UT | Electro relay sensor CTVT Horizont 2.5-25A US | Electronic motor relay sensor CTVT Horizontal 2.5-25A US | Sensor | New | Yes
43 | LTMTCTV100UT | Electro relay sensor CTVT Horizont 10-100A US | Electronic motor relay sensor CTVT Horizontal 10-100A US | Sensor | New | Yes
44 | LTM9CU10 | LTMR/LTME TO LTMCU HMI DEVICE CABLE 1M | Same as Tesys T cable | Cable- Expansion/HMI | Tesys T | Yes
45 | LTM9CU30 | LTMR/LTME TO LTMCU HMI DEVICE CABLE 3M | Same as Tesys T cable | Cable | Tesys T | Yes
46 | LTMCUF | Electro relay screen | Electronic motor relay screen | HMI | Tesys T | Yes

## Settings-Interlocks
Device Configuration | 1 - LTMTCT3L 2 - LTMTCTV3L 3 - LTMTCT3T 4 - LTMTCTV3T 15 - LTMTCTV3UT |  | 5 - LTMTCT25L 6 - LTMTCTV25L 7 - LTMTCT25T 8 - LTMTCTV25T 16 - LTMTCTV25UT |  | 9 - LTMTCT100L 10 - LTMTCTV100L 11 - LTMTCT100T 12 - LTMTCTV100T 17 - LTMTCTV100UT |  | 13 - LTMTCT70L 14 - LTMTCTV70L
| Range | Default | Range | Default | Range | Default | Range | Default
Phase CT Primary | 1 to 1000 | 1 | 1 to 1000 | 1 | 1 | 1 | 1 | 1
Phase CT Secondary | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Phase CT secondary passes | 1 to 10 | 1 | 1 to 10 | 1 | 1 | 1 | 1 | 1
Full load Current | 0.1 to 1000.0 | 0.3 | 0.3 to 1000.0 | 2.5 | 1.0 to 100.0 | 10 | 0.7 to 70 | 7
Speed 2 CT primary | 1 to 1000 | 1 | 1 to 1000 | 1 | 1 | 1 | 1 | 1
Speed 2 CT secondary | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Speed 2 CT secondary passes | 1 to 10 | 1 | 1 to 10 | 1 | 1 | 1 | 1 | 1
Speed 2 Full Load Current | 0.1 to 1000.0 | 0.3 | 0.3 to 1000.0 | 2.5 | 1.0 to 100.0 | 10 | 0.7 to 70 | 7
IFLC Min & Max range calculation
CT Type | 1 - LTMTCT3L 2 - LTMTCTV3L 3 - LTMTCT3T 4 - LTMTCTV3T 15 - LTMTCTV3UT |  | 5 - LTMTCT25L 6 - LTMTCTV25L 7 - LTMTCT25T 8 - LTMTCTV25T 16 - LTMTCTV25UT |  | 9 - LTMTCT100L 10 - LTMTCTV100L 11 - LTMTCT100T 12 - LTMTCTV100T 17 - LTMTCTV100UT |  | 13 - LTMTCT70L 14 - LTMTCTV70L
CT Primary | 1500 |  | 1000 |  | 1 | CT Primary should be always 1 | 1 | CT Primary should be always 1
CT secondary | 1 | if CT primary is >= 5, then allow CT secondary as 5, else 1 | 5 | if CT primary is >1, then only Allow CT Secondary = 5 | 1 | CT Secondary should be always 1 | 1 | CT Secondary should be always 1
CT secondary passes | 1 |  | 1 |  | 1 |  | 1
IFLC Min range | 450 |  | 500 |  | 10 |  | 7
IFLC Max Range | 1000 |  | 1000 |  | 100 |  | 70

## EIP DETAILS
|  | Tesys T |  | Tera |  |  | Tera Data
IDENTITY OBJECT
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü | NA | ü | NA |  | The Identity Objects implementation revision. Returns 0x02
02h | Maximum instance | ü | NA | ü | NA |  | The largest instance number. Returns 0x01.
03h | Number of instances | ü | NA | ü | NA |  | The number of object instances. Returns 0x01.
06h | Max Class Attribute | ü | NA | û | NA
07h | Max Instance Attribute | ü | NA | û | NA
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance : 1 | Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Vendor Id | ü |  | ü | NA |  | Vendor ID (243: Schneider Electri)
02h | Device Type | ü |  | ü | NA |  | Motor starter profile (22)
03h | Device code | ü |  | ü | NA |  | LTMTEFM: 0x3401 LTMTEBD: 0x3402
04h | Identity Revision | ü |  | ü | NA |  | Product version. product communication version: 1.1
05h | Identity Status | ü |  | ü | NA |  | Current status of the device
06h | DeviceSerial Number | ü |  | ü | NA |  | Based on device entity and MAC: • 0x20: Byte 0 (Entity ID for TeSys T) • Bytes 1-3: Last 3 bytes of MAC address
07h | Product Name | ü |  | ü | NA |  | Commercial reference
Instance Services
|  | Access |  | Access
ID | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
05h | Reset | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
MESSAGE ROUTER OBJECT
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | û
02h | Maximum instance | ü |  | û
03h | Number of instances | ü |  | û
04h | Optional Attribute list | ü |  | û
05h | Optional Service list | ü |  | û
06h | Max Class Attributes | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Object List | ü |  | û
02h | Max connection supported | ü |  | û
03h | Number of active connections | ü |  | û
04h | Active connection list | ü |  | û
64h | Total incoming Class 1 packets received during the last second | ü |  | û
65h | Total outgoing Class 1 packets sent during the last second | ü |  | û
66h | Total incoming Class 3 packets received during the last second | ü |  | û
67h | Total outgoing Class 3 packets sent during the last second | ü |  | û
68h | Total incoming unconnected packets received during the last second | ü |  | û
69h | Total outgoing unconnected packets sent during the last second | ü |  | û
6Ah | Total incoming EtherNet/IP packets received during the last second | ü |  | û
6Bh | Total outgoing EtherNet/IP packets sent during the last second | ü |  | û
6Ch | Total incoming Class 1 packets received | ü |  | û
6Dh | Total outgoing Class 1 packets sent | ü |  | û
6Eh | Total incoming Class 3 packets received | ü |  | û
6Fh | Total incoming Class 3 packets Invalid Parameter Value | ü |  | û
70h | Total incoming Class 3 packets invalid format | ü |  | û
71h | Total outgoing Class 3 packets sent | ü |  | û
72h | Total incoming unconnected packets received | ü |  | û
73h | Total incoming unconnected packets Invalid Parameter Value | ü |  | û
74h | Total incoming unconnected packets Invalid Format | ü |  | û
75h | Total outgoing unconnected packets sent | ü |  | û
76h | Total incoming EtherNet/IP packets | ü |  | û
77h | Total outgoing EtherNet/IP packets | ü |  | û
Instance Services
|  | Access |  | Access
ID | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Ah | Multiple Service | ü |  | û
0Eh | Get_Attributes_Single |  |  | û
ASSEMBLY OBJECT
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü | NA
02h | Maximum instance | ü |  | ü | NA |  | The maximum numeric value of the instance number. Returns 117
03h | Number of instances | ü |  | ü | NA |  | The number of supported assembly instances.
04h | Optional Attribute List | ü |  | û | NA
06h | Max Class Attribute | ü |  | û | NA
07h | Max Instance Attribute | ü |  | û | NA
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
0Eh | Get_Attributes_single | ü |  | ü
10h | Set_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
03h | Assembly Instance Data | ü |  | ü | ü |  | Instance data returned as an array of bytes. Access is Read Only for the input data assemblies and Read/Write for the output data assemblies.
04h | Instance Data Size | ü |  | û | û
Instance Services
|  | Access |  | Access
ID | Description | Parameter options |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set_Attributes_Single | ü |  | ü
CONNECTION MANAGER OBJECT
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü | NA |  | The Connection Manager implementation revision. Returns 0x01.
02h | Maximum instance | ü |  | ü | NA |  | The largest instance number. Returns 0x01.
03h | Number of instances | ü |  | ü | NA |  | The number of object instances. Returns 0x01.
04h | Optional Attribute List | ü |  | û | NA
06h | Max Class Attribute | ü |  | û | NA
07h | Max Instance Attribute | ü |  | û | NA
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Incoming Forward Open requests count | ü |  | ü | ü |  | Total number of incoming connection open requests.
02h | Forward Open Format Unsuccessful count | ü |  | ü | ü |  | The number of Forward Open requests rejected because of the unexpected format of the Forward Open request
03h | Forward Open Resource Unsuccessful count | ü |  | ü | ü |  | The number of Forward Open requests rejected because of insufficient resources
04h | Forward Open Parameter Value count | ü |  | ü | ü |  | The number of Forward Open requests rejected because of the parameter value sent with Forward Open.
05h | Incoming Forward Close requests count | ü |  | ü | ü |  | Total number of incoming connection close requests
06h | Forward Close Format Unsuccessful count | ü |  | ü | ü |  | The number of Forward Close requests that has invalid format
07h | Forward Close Matching Unsuccessful count | ü |  | ü | ü |  | The number of Forward Close requests that could not be matched to an active connection.
08h | Timed out Connections count | ü |  | ü | ü |  | The number of connections that has timed out because the other side stopped producing or there was a network interruption.
Instance Services
|  | Access |  | Access
ID | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
02h | Set Attributes All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set Attributes Single | ü |  | û
4Eh | Forward close | ü |  | ü
52h | Unconnected Send | ü |  | û
54h | Forward Open | ü |  | ü
5Ah | Get Conncetion | ü |  | û
5Bh | Large Forward Open | ü |  | û
QoS OBJECT
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü | NA
02h | Maximum instance | ü |  | ü | NA
03h | Number of instances | ü |  | ü | NA
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
04h | DSCP Urgent | ü | ü | ü | ü
05h | DSCP Scheduled | ü | ü | ü | ü
06h | DSCP high | ü | ü | ü | ü
07h | DSCP low | ü | ü | ü | ü
08h | DSCP Explicit | ü | ü | ü | ü
Instance Services
Access
ID | Description |  |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set_Attributes_Single | ü |  | ü
TCP/IP OBJECT
Class Attributes
|  |  |  | Access |  |  | Info
Attribute ID | Description |  |  | get | set
01h | Revision | ü |  | ü | NA |  | The TCP/IP Object implementation revision. Returns 0x04.
02h | Maximum instance | ü |  | ü | NA |  | Indicate that there is only one host IP address. Returns 0x01.
03h | Number of instances | ü |  | ü | NA |  | The number of object instances. Returns 0x01.
04h | Optional Attribute List | ü |  | û | NA
06h | Max Class Attribute | ü |  | û | NA
07h | Max Instance Attribute | ü |  | û | NA
Class Services
Access
Service code | Description |  |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
û
01h | Configuration Status | ü |  | ü | û |  | Indicates whether you configured TCP/IP object and its parameters or not.
02h | Configuration Capability | ü |  | ü | û
03h | Configuration Control | ü |  | ü | û
04h | Physical link | ü |  | ü | û
05h | Interface Configuration | ü |  | ü | û |  | TCP/IP parameters including the following: • DWORD containing the device IP address. • DWORD containing the subnet mask. • DWORD containing the gateway address. • DWORD containing the name server IP address.: Value of 0 indicates no name server address has been configured. • DWORD containing the second name server IP address.:Value of 0 indicates no name server address has been configured. • WORD containing number of ASCII characters in the domain name if applicable
06h | Host Name | ü |  | ü | û |  | Data type is :STRING
07h | Safety Network Number |  |  | û | û
08h | TTL Value |  |  | û | û
09h | MCast Config |  |  | û | û
0Ah | Select Acd |  |  | û | û
0Bh | Last Conflict Detected |  |  | û | û
0Ch | EIP Quick Connect |  |  | û | û
0Dh | Encapsulation Inactivity Timeout | ü |  | ü | ü |  | 120
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set_Attributes_Single |  |  | ü
ETHERNET LINK OBJECT
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü |  |  | The Ethernet Link Object implementation revision. Returns 0x04
02h | Maximum instance | ü |  | ü |  |  | Returns 0x02 to represent two Ethernet port instances.
03h | Number of instances | ü |  | ü |  |  | The number of object instances. Returns 0x02 to represent two Ethernet port instances.
04h | Optional Attribute List | ü |  | û
06h | Max Class Attribute | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Interface Speed | ü |  | ü | û
02h | Interface Flag | ü |  | ü | û
03h | Physical Address | ü |  | ü | û
04h | Interface Counters | ü |  | ü | û
05h | Media Counters | ü |  | ü | û
06h | Interface Control | ü |  | ü | ü
07h | Interface Type | ü |  | ü | û
08h | Interface State | ü |  | ü | û
09h | Admin State | ü |  | ü | ü
0Ah | Interace Label | ü |  | ü | û
0Bh | Interface Capability | ü |  | ü | û
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set_Attributes_Single | ü |  | ü
4Ch | Get_and_clear | ü |  | ü
Control Supervisor Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü
02h | Maximum instance | ü |  | ü
03h | Number of instances | ü |  | ü
06h | Max Class Attribute | ü |  | ü
07h | Max Instance Attribute | ü |  | ü
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
03h | Run 1 | ü |  | ü | ü
04h | Run 2 | ü |  | ü | ü
06h | State | ü |  | ü
07h | Running 1 | ü |  | ü
08h | Running 2 | ü |  | ü
09h | Ready | ü |  | ü
0Ah | Tripped | ü |  | ü
0Bh | Alarm | ü |  | ü
0Ch | Trip Reset | ü |  | ü | ü
0Dh | Trip Code | ü |  | ü
0Eh | Alarm code | ü |  | ü
0Fh | Control from Network | ü |  | ü
10h | Net Trip Mode | ü
14h | Net idle Mode | ü
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
05h | Reset | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set_Attributes_Single | ü |  | ü
OVERLOAD Object
Class Attributes
Access
Attribute ID | Description |  |  | get | set
01h | Revision | ü |  | ü
02h | Maximum instance | ü |  | ü
03h | Number of instances | ü |  | ü
06h | Max Class Attribute | ü |  | ü
07h | Max Instance Attribute | ü |  | ü
Class Services
Access
Service code | Description |  |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
Access
Attribute ID | Description |  |  | get | set
01h | Attribute Count | ü |  | ü
02h | Attribute List | ü |  | not supported
03h | Trip FLC set | ü |  | not supported | Not supported
04h | Trip Class | ü |  | ü | supported
05h | Avg Current | ü |  | ü
06h | %ph Imbal | ü |  | ü
07h | %thermal | ü |  | ü
08h | IL1 Current | ü |  | ü
09h | IL2 Current | ü |  | ü
0Ah | IL3 Current | ü |  | ü
0Bh | Ground Current | ü |  | ü
65h | IL1 Current | ü |  | ü
66h | IL2 Current | ü |  | ü
67h | IL3 Current | ü |  | ü
68h | Ground Current | ü |  | ü
69h | IL1 Current Ratio | ü |  | ü
6Ah | IL2 Current Ratio | ü |  | ü
6Bh | IL3 Current Ratio | ü |  | ü
6Ch | IAV Average Current Ratio | ü |  | ü
6Dh | Thermal Capacity Level | ü |  | ü
6Eh | Ground Current | ü |  | ü
6Fh | Current phase imbalance | ü |  | ü
70h | Time to trip | ü |  | ü
71h | Time to Reset | ü |  | ü
7Fh | Single/Three Ph | ü |  | ü | ü
80h | TripFLCSet | ü |  | ü | ü
81h | Trip Class | ü |  | ü | ü
84h | Thermal Alarm Level | ü |  | ü | ü
85h | PL Inhibit Time | ü |  | not supported | not supported
86h | PL Trip Delay | ü |  | ü | ü
88h | Ground Current Trip Delay | ü |  | ü | ü
89h | Ground Current Trip Level | ü |  | ü | ü
8Ah | Ground Current Alarm Level | ü |  | ü | ü
8Bh | Stall Enabled Time | ü |  | not supported | Not supported
8Ch | Stall Trip Level | ü |  | ü | ü
8Eh | Jam Trip Delay | ü |  | ü | ü
8Fh | Jam Trip Level | ü |  | ü | ü
90h | Jam Alarm Level | ü |  | ü | ü
92h | UL Trip Delay | ü |  | ü | ü
93h | UL Trip Level | ü |  | ü | ü
94h | UL Alarm Level | ü |  | ü | ü
95h | CI Inhibit Time | ü |  | not supported | not supported
96h | CI Trip Delay | ü |  | ü | ü
97h | CI Trip Level | ü |  | ü | ü
98h | CI Alarm Level | ü |  | ü | ü
B2h | CT Ratio | ü |  | ü | ü
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | ü
10h | Set_Attributes_Single | ü |  | ü
| PKW Object |  |  | PKW feature is supported in Tera
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | û
02h | Maximum instance | ü |  | û
03h | Number of instances | ü |  | û
06h | Max Class Attribute | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Request Object | ü |  | û
02h | Response Object | ü |  | û
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | û
10h | Set_Attributes_Single | ü |  | û
| TeSys T Monitoring Control Object |  |  | Monitoring Data of Tesys T is Mapped to Tera
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü
02h | Maximum instance | ü |  | ü
03h | Number of instances | ü |  | ü
06h | Max Class Attribute | ü |  | ü
07h | Max Instance Attribute | ü |  | ü
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access |  | Default modbus register address
Attribute ID | Description | get | set | get | set
01h | TeSys T Monitoring Word 0 Address | ü |  | ü | ü | 455
02h | TeSys T Monitoring Word 1 Address | ü |  | ü | ü | 456
03h | TeSys T Monitoring Word 2 Address | ü |  | ü | ü | 457
04h | TeSys T Monitoring Word 3 Address | ü |  | ü | ü | 458
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
0Eh | Get_Attributes_Single | ü |  | û
10h | Set_Attributes_Single | ü |  | û
EtherNet/IP Interface Diagnostic Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | û
02h | Maximum instance | ü |  | û
03h | Number of instances | ü |  | û
04h | Optional Attribute list | ü |  | û
05h | Optional Service list | ü |  | û
06h | Max Class Attributes | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set |  | limits
01h | Protocols supported | ü |  | û
02h | Connection diagnostics | ü |  | û
03h | I/O Messaging Diagnostics | ü |  | û
04h | Explicit Messaging Diagnostics | ü |  | û
05h | Communication Capacity | ü |  | û
06h | Bandwidth Diagnostics | ü |  | û
07h | Modbus Diagnostic | ü |  | û
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
10h | Set_Attributes_Single | ü |  | û
I/O Connection Diagnostic Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | û
02h | Maximum instance | ü |  | û
03h | Number of instances | ü |  | û
04h | Optional Attribute list | ü |  | û
05h | Optional Service list | ü |  | û
06h | Max Class Attributes | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set |  | limits
01h | I/O Communication Diagnostics | ü |  | û
02h | Connection diagnostics | ü |  | û
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
4Ch | Get_and_clear | ü |  | û
Explicit Connection Diagnostic Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | û
02h | Maximum instance | ü |  | û
03h | Number of instances | ü |  | û
04h | Optional Attribute list | ü |  | û
05h | Optional Service list | ü |  | û
06h | Max Class Attributes | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Originator Connection ID | ü |  | û
02h | Originator IP | ü |  | û
03h | Originator TCP Port | ü |  | û
04h | Target Connection ID | ü |  | û
05h | Target IP | ü |  | û
06h | Target TCP Port | ü |  | û
07h | Message Send Counter | ü |  | û
08h | Message Receive Counter | ü |  | û
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
Explicit Connection Diagnostic List Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | û
02h | Maximum instance | ü |  | û
03h | Number of instances | ü |  | û
04h | Optional Attribute list | ü |  | û
05h | Optional Service list | ü |  | û
06h | Max Class Attributes | ü |  | û
07h | Max Instance Attribute | ü |  | û
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | û
0Eh | Get_Attributes_Single | ü |  | û
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Number of Connections | ü |  | û
02h | Explicit Messaging Connections Diagnostic List | ü |  | û
Instance Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
08h | Create | ü |  | û
09h | Delete | ü |  | û
33h | Explicit Connections Diagnostic Read | ü |  | û
LLDP Management Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü | not supported
02h | Maximum instance | ü |  | ü | not supported
03h | Number of instances | ü |  | ü | not supported
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All | ü |  | ü
0Eh | Get_Attributes_Single | ü |  | ü
Instance Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
ü
01h | LDP Enable(LLDP Enable Array Length, LLDP Enable Array) | ü |  | ü | ü
02h | msgTxInterval | ü |  | ü | ü
03h | MsgTxHold | ü |  | ü | ü
04h | LLDP Datastore | ü |  | ü | û
05h | Last Change | ü |  | ü | û
Services
|  | Access |  | Access
Service code | Description | Class | Instance | Class | Instance
01h | Get_Attributes_All | ü | ü | ü | ü
0Eh | Get_Attributes_Single | ü | ü | ü | ü
10h | Set_Attributes_Single |  |  | û | ü
LLDP Data Table Object
Class Attributes
|  | Access |  | Access
Attribute ID | Description | get | set | get | set
01h | Revision | ü |  | ü | not supported
02h | Maximum instance | ü |  | ü | not supported
03h | Number of instances | ü |  | ü | not supported
Class Services
|  | Access |  | Access
Service code | Description | Parameter options |  | Parameter options
01h | Get_Attributes_All |  |  | ü
0Eh | Get_Attributes_Single |  |  | ü
0x11 | Find Next Object Instance |  |  | ü
Instance Attributes
Access
Attribute ID | Description |  |  | get | set
01h | Ethernet Link Instance Number | ü |  | ü | not supported
02h | MAC Address | ü |  | ü | not supported
03h | Interface Label | ü |  | ü | not supported
04h | Time to live | ü |  | ü | not supported
05h | System Capabilities TLV,System Capabilities, Enabled Capabilities | ü |  | ü | not supported
06h | IPv4 Management Addresses:Management Address Count,Management Address | ü |  | ü | not supported
07h | CIP Identification: Vendor ID,Device Type,Product Code,Major Revison,Minor Revision,CIP Servial Number | ü |  | ü | not supported
08h | Additional Ethernet Capabilities | ü |  | ü | not supported
09h | Last Change | ü |  | ü | not supported
Services
Access
Service code | Description |  |  | Class | Instance
01h | Get_Attributes_All | ü |  | ü | ü
0Eh | Get_Attributes_Single | ü |  | ü | ü
10h | Find_Next_Object_Instance |  |  | ü | not supported

## Ethernet settings
| Attribute Name | Data Type | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | Register Address | Register | Data Address | Function Codes | Svd | Default Value | Units | EIP attribute address (Decimal) | EIP attribute address(Hex) | Remarks
Ethernet Settings
[17 empty] | Decimal 136->01-> (starting address) | Hex 88->01-> (starting address) |  | HMI Allowed Read/Write Access for Configuration
Port Configuration*********
| Protocol selection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44876 | 4876 | 4875 | 0x03,0x06,0x10 | Y | 1 | NA | 1 | 1 | 0 - Modbus/TCP 1 - Ehernet/IP 2- Profinet | Y
| Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44877 | 4877 | 4876 | 0x03,0x06,0x10 | Y | 0 | NA | 2 | 2 | 0- RSTP 1- DLR 2- MRP | N
| EIP Device Profile Selection | UINT16 | 2 | 1 | 0 | 12 | 1 | 1 | RW | 44878 | 4878 | 4877 | 0x03,0x06,0x10 | Y | 0 | NA | 3 | 3 | 0: Tera Profile 1: Tera Basic Overload 2: Tera Extended Overload 3: Tera Basic Motor Starter 4: Tera Extended Contactor 5: Tera Extended Motor Starter 1 6: Tera Extended Motor Starter 2 7: Tera LTMR Control and Monitoring 8: Tera PKW 9: Tera PKW and Extended Motor Starter 10: Tera PKW and LTMR Management 11: Tera E_TeSys T Fast Access 12: Tera EIOS_TeSys T | N | FB access from EIP is needed but not from Modbus TCP/Even from Modbus
| IP address Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44879 | 4879 | 4878 | 0x03,0x06,0x10 | Y | 169 | NA | 4 | 4 |  | Y
| IP address Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44880 | 4880 | 4879 | 0x03,0x06,0x10 | Y | 254 | NA | 5 | 5 |  | Y
| IP address Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44881 | 4881 | 4880 | 0x03,0x06,0x10 | Y | 2nd Last Byte of MAC | NA | 6 | 6 |  | Y
| IP address Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44882 | 4882 | 4881 | 0x03,0x06,0x10 | Y | Last Byte Of MAC | NA | 7 | 7 |  | Y
| Subnet Mask Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44883 | 4883 | 4882 | 0x03,0x06,0x10 | Y | 255 | NA | 8 | 8 |  | Y
| Subnet Mask Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44884 | 4884 | 4883 | 0x03,0x06,0x10 | Y | 255 | NA | 9 | 9 |  | Y
| Subnet Mask Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44885 | 4885 | 4884 | 0x03,0x06,0x10 | Y | 0 | NA | 10 | A |  | Y
| Subnet Mask Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44886 | 4886 | 4885 | 0x03,0x06,0x10 | Y | 0 | NA | 11 | B |  | Y
| Default gateway Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44887 | 4887 | 4886 | 0x03,0x06,0x10 | Y | 0 | NA | 12 | C |  | Y
| Default gateway Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44888 | 4888 | 4887 | 0x03,0x06,0x10 | Y | 0 | NA | 13 | D |  | Y
| Default gateway Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44889 | 4889 | 4888 | 0x03,0x06,0x10 | Y | 0 | NA | 14 | E |  | Y
| Default gateway Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44890 | 4890 | 4889 | 0x03,0x06,0x10 | Y | 0 | NA | 15 | F |  | Y
| NTP/SNTP primary server Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44891 | 4891 | 4890 | 0x03,0x06,0x10 | Y | 0 | NA | 16 | 10 |  | N
| NTP/SNTP primary server Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44892 | 4892 | 4891 | 0x03,0x06,0x10 | Y | 0 | NA | 17 | 11 |  | N
| NTP/SNTP primary server Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44893 | 4893 | 4892 | 0x03,0x06,0x10 | Y | 0 | NA | 18 | 12 |  | N
| NTP/SNTP primary server Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44894 | 4894 | 4893 | 0x03,0x06,0x10 | Y | 0 | NA | 19 | 13 |  | N
| SNTP selection | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44895 | 4895 | 4894 | 0x03,0x06,0x10 | Y | 0 | NA | 20 | 14 | 0:Manual(Wepage),1:sntp2: from FB Protocol | Y
| SNTP Time Zone | UINT16 | 2 | 1 | 1 | 28 | 1 | 1 | RW | 44896 | 4896 | 4895 | 0x03,0x06,0x10 | N | 19 | NA | 21 | 15 | time zone: total 28 time zone | Y |  | Value | Time Zone
| IP Configuration | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 44897 | 4897 | 4896 | 0x03,0x06,0x10 | Y | 0 | NA | 22 | 16 | 0: DHCP 1: Reserved 2: Manual | Y |  | 1 | UTC−12:00
| Modbus TCP Endian Selection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44898 | 4898 | 4897 | 0x03,0x06,0x10 | N | 0 | NA | 23 | 17 | 0: Big Endian 1: Little Endian | Y |  | 2 | UTC−11:00
| Modbus TCP Unit ID | UINT16 | 2 | 1 | 1 | 255 | 1 | 1 | RW | 44899 | 4899 | 4898 | 0x03,0x06,0x10 | N | 255 | NA | 24 | 18 |  | N |  | 3 | UTC−10:00
| SNMP V3 ******** | [20 empty] | 4 | UTC−09:00
| SNMP Enable/Disable | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44900 | 4900 | 4899 | 0x03,0x06,0x10 | Y | 0 | NA | 25 | 19 | 0-DISABLE 1-ENABLE | N |  | 5 | UTC−08:00
| Version | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44901 | 4901 | 4900 | 0x03,0x06,0x10 | Y | 0 | NA | 26 | 1A | 0 - V3 1 - V2 | N |  | 6 | UTC−07:00
| Name | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | RW | 44902 | 4902 | 4901 | 0x03,0x06,0x10 | Y | 0 | NA | 27 | 1B | This is same as Motor Tag Name | N |  | 7 | UTC−06:00
| Auth algorithm | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44934 | 4934 | 4933 | 0x03,0x06,0x10 | Y | 0 | NA | 59 | 3B | MD5(MD5,SHA,SHA224,SHA256,SHA384,SHA512) | N |  | 8 | UTC−05:00
| Auth password | UINT16 | 64 | 32 | 0 | 65535 | 1 | 1 | RW | 44935 | 4935 | 4934 | 0x03,0x06,0x10 | Y | 0 | NA | 60 | 3C |  | N |  | 9 | UTC−04:00
| Privacy Algorithm | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44967 | 4967 | 4966 | 0x03,0x06,0x10 | Y | 0 | NA | 92 | 5C | DES(DES,AES,AES192,AES256,3DES) | N |  | 10 | UTC−03:00
| Privacy password | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44968 | 4968 | 4967 | 0x03,0x06,0x10 | Y | 0 | NA | 93 | 5D |  | N |  | 11 | UTC−02:00
| Trap Receipt | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44969 | 4969 | 4968 | 0x03,0x06,0x10 | Y | 0 | NA | 94 | 5E |  | N |  | 12 | UTC−01:00
| SNMP port | UINT16 | 2 | 1 | 1 | 65535 | 1 | 1 | RW | 44970 | 4970 | 4969 | 0x03,0x06,0x10 |  | 161 |  | 95 | 5F | 161 | N |  | 13 | UTC+00:00
| SNMP Read Community | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44971 | 4971 | 4970 | 0x03,0x06,0x10 |  | 0 |  | 96 | 60 | Blank | N |  | 14 | UTC+01:00
| SNMP Write Community | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44972 | 4972 | 4971 | 0x03,0x06,0x10 |  | 0 |  | 97 | 61 | Blank | N |  | 15 | UTC+02:00
| SNMP Trap Community | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44973 | 4973 | 4972 | 0x03,0x06,0x10 |  | 0 |  | 98 | 62 |  | N |  | 16 | UTC+03:00
| USM User | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44974 | 4974 | 4973 | 0x03,0x06,0x10 |  | 0 |  | 99 | 63 | Blank | N |  | 17 | UTC+04:00
| Cold Start Trap | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44975 | 4975 | 4974 | 0x03,0x06,0x10 |  | 0 |  | 100 | 64 | 0-DISABLE 1-ENABLE | N |  | 18 | UTC+05:00
| Warm Start Trap | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44976 | 4976 | 4975 | 0x03,0x06,0x10 |  | 0 |  | 101 | 65 | 0-DISABLE 1-ENABLE | N |  | 19 | UTC+05:30
| Link Down Trap | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44977 | 4977 | 4976 | 0x03,0x06,0x10 |  | 0 |  | 102 | 66 | 0-DISABLE 1-ENABLE | N |  | 20 | UTC+06:00
| Link up Trap | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44978 | 4978 | 4977 | 0x03,0x06,0x10 |  | 0 |  | 103 | 67 | 0-DISABLE 1-ENABLE | N |  | 21 | UTC+07:00
| Authentication failer Trap | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44979 | 4979 | 4978 | 0x03,0x06,0x10 |  | 0 |  | 104 | 68 | 0-DISABLE 1-ENABLE | N |  | 22 | UTC+08:00
[17 empty] | 105 | 69 |  | N |  | 23 | UTC+09:00
| HTTPS | [18 empty] | N |  | 24 | UTC+09:30
| Reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 44980 | 4980 | 4979 | 0x03,0x06,0x10 | Y | 0 | NA | 105 | 69 |  | N |  | 25 | UTC+10:00
| Port number | UINT16 | 2 | 1 | 1 | 65535 | 1 | 1 | RW | 44981 | 4981 | 4980 | 0x03,0x06,0x10 | Y | 443 | NA | 106 | 6A |  | N |  | 26 | UTC+11:00
[20 empty] | N |  | 27 | UTC+12:00
| DPWS | [18 empty] | N |  | 28 | UTC+13:00
| Enable/disable | UINT16 | 2 | 1 | 0 | 1 | 1 |  | RW | 44982 | 4982 | 4981 | 0x03,0x06,0x10 | Y | 1 | NA | 107 | 6B | 0=disable;1= enable | N
| Silent Mode | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44983 | 4983 | 4982 | 0x03,0x06,0x10 | Y | 0 | NA | 108 | 6C | 0 = silent; 1= non silent | N
| Port | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 44984 | 4984 | 4983 | 0x03,0x06,0x10 | Y | 5357 | NA | 109 | 6D | Port number = 5357 | N
| FDR PLC | [18 empty] | N
| FDR Function | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44985 | 4985 | 4984 | 0x03,0x06,0x10 | Y | 1 | NA | 110 | 6E | 0 - Disable 1 - Enable | N
| FDR Auto backup Enabled | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44986 | 4986 | 4985 | 0x03,0x06,0x10 | Y | 1 | NA | 111 | 6F | 0 - Disable 1 - Enable | N
| FDR auto backup period Settings | UINT16 | 2 | 1 | 30 | 3600 | 1 | 1 | RW | 44987 | 4987 | 4986 | 0x03,0x06,0x10 | Y | 120 | Seconds | 112 | 70 |  | N
| Communication Configuraiton******** | [18 empty] | N
| client IP Address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44988 | 4988 | 4987 | 0x03,0x06,0x10 | Y | 192 | NA | 113 | 71 | 0 | Y
| Client IP Address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44989 | 4989 | 4988 | 0x03,0x06,0x10 | Y | 168 | NA | 114 | 72 | 0 | Y
| Client IP Address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44990 | 4990 | 4989 | 0x03,0x06,0x10 | Y | 1 | NA | 115 | 73 | 0 | Y
| Client IP Address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44991 | 4991 | 4990 | 0x03,0x06,0x10 | Y | 100 | NA | 116 | 74 | 0 | Y
| Communication timeout | UINT16 | 2 | 1 | 0 | 100 | 1 | 1 | RW | 44992 | 4992 | 4991 | 0x03,0x06,0x10 | Y | 2 | Seconds | 117 | 75 |  | Y
| numeric or string for NTP primary and secondary(for internal Purpose) | UINT16 | 2 | 1 | 0 | 3 | 1 | 1 | RW | 44993 | 4993 | 4992 | 0x03,0x06,0x10 | Y | 0 | NA | 118 | 76 | 0- Both Pri and Sec: Str name 1- Pri as IP and Sec as Str name 2- Pri as Str name and Sec as IP 3- Pri as IP and Sec as IP | N
| Modbus TCP port | UINT16 | 2 | 1 | 1 | 65535 | 1 | 1 | RW | 44994 | 4994 | 4993 | 0x03,0x06,0x10 | Y | 502 | NA | 119 | 77 |  | N
| Broadcast Storm Protection Enable/Disable | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44995 | 4995 | 4994 | 0x03,0x06,0x10 | Y | 0 | NA | 120 | 78 | 0 - Disable 1 - Enable | N
| Broadcast Storm Protection | UINT16 | 2 | 1 | 0 | 5 | 1 | 1 | RW | 44996 | 4996 | 4995 | 0x03,0x06,0x10 | Y | 0 | NA | 121 | 79 | 0 - lowest (Display Name and not rate)1000 packets/second 1 - low: 2000 packets/sec 2 - Medium Low:3000 packets/seconds 3 - Medium High 4 - High 5 - Highest | N
Only applicable for Webservices No Read and Write from Modbus / EIP | IP address allowlist (not needed to update over Modbus register) have kept here for future development reference only | [18 empty] | N
| IP filter selection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44997 | 4997 | 4996 | 0x03,0x06,0x10 | Y | 0 | NA | 122 | 7A | 0 - Disable 1 - Enable | N
| IP Filtering Global Access List (not needed to update over Modbus register) have kept here for future development reference only | [18 empty] | N
| Access Level for first IP allow list | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 44998 | 4998 | 4997 | 0x03,0x06,0x10 | Y | 0 | NA | 123 | 7B | 0 - None 1 - Read/Write | N
| IP allowlist range1 address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 44999 | 4999 | 4998 | 0x03,0x06,0x10 | Y | 0 | NA | 124 | 7C |  | N
| IP allowlist range1 address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45000 | 5000 | 4999 | 0x03,0x06,0x10 | Y | 0 | NA | 125 | 7D |  | N
| IP allowlist range1 address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45001 | 5001 | 5000 | 0x03,0x06,0x10 | Y | 0 | NA | 126 | 7E |  | N
| IP allowlist range1 address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45002 | 5002 | 5001 | 0x03,0x06,0x10 | Y | 0 | NA | 127 | 7F |  | N
| NTP/SNTP secondary server Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45003 | 5003 | 5002 | 0x03,0x06,0x10 | Y | 0 | NA | 128 | 80 |  | N
| NTP/SNTP secondary server Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45004 | 5004 | 5003 | 0x03,0x06,0x10 | Y | 0 | NA | 129 | 81 |  | N
| NTP/SNTP secondary server Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45005 | 5005 | 5004 | 0x03,0x06,0x10 | Y | 0 | NA | 130 | 82 |  | N
| NTP/SNTP secondary server Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45006 | 5006 | 5005 | 0x03,0x06,0x10 | Y | 0 | NA | 131 | 83 |  | N
| IP Filtering Exceptional List: if define individaul IP address takes priority(not needed to update over Modbus register) have kept here for future development reference only | [18 empty] | N
| Access Level for first IP | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45007 | 5007 | 5006 | 0x03,0x06,0x10 | Y | 0 | NA | 132 | 84 | 0 - None 1 - Read/Write | N
| IP allowlist range1 address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45008 | 5008 | 5007 | 0x03,0x06,0x10 | Y | 0 | NA | 133 | 85 |  | N
| IP allowlist range1 address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45009 | 5009 | 5008 | 0x03,0x06,0x10 | Y | 0 | NA | 134 | 86 |  | N
| IP allowlist range1 address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45010 | 5010 | 5009 | 0x03,0x06,0x10 | Y | 0 | NA | 135 | 87 |  | N
| IP allowlist range1 address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45011 | 5011 | 5010 | 0x03,0x06,0x10 | Y | 0 | NA | 136 | 88 |  | N
| DNS Primary Server address Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45012 | 5012 | 5011 | 0x03,0x06,0x10 | Y | 0 | NA | 137 | 89 |  | N
| DNS Primary Server address Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45013 | 5013 | 5012 | 0x03,0x06,0x10 | Y | 0 | NA | 138 | 8A |  | N
| DNS Primary Server address Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45014 | 5014 | 5013 | 0x03,0x06,0x10 | Y | 0 | NA | 139 | 8B |  | N
| DNS Primary Server address Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45015 | 5015 | 5014 | 0x03,0x06,0x10 | Y | 0 | NA | 140 | 8C |  | N
| Access Level for second IP | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45016 | 5016 | 5015 | 0x03,0x06,0x10 | Y | 0 | NA | 141 | 8D | 0 - None 1 - Read/Write | N
| IP allowlist range2 address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45017 | 5017 | 5016 | 0x03,0x06,0x10 | Y | 0 | NA | 142 | 8E |  | N
| IP allowlist range2 address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45018 | 5018 | 5017 | 0x03,0x06,0x10 | Y | 0 | NA | 143 | 8F |  | N
| IP allowlist range2 address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45019 | 5019 | 5018 | 0x03,0x06,0x10 | Y | 0 | NA | 144 | 90 |  | N
| IP allowlist range2 address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45020 | 5020 | 5019 | 0x03,0x06,0x10 | Y | 0 | NA | 145 | 91 |  | N
| DNS Secondary Server address Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45021 | 5021 | 5020 | 0x03,0x06,0x10 | Y | 0 | NA | 146 | 92 |  | N
| DNS Secondary Server address Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45022 | 5022 | 5021 | 0x03,0x06,0x10 | Y | 0 | NA | 147 | 93 |  | N
| DNS Secondary Server address Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45023 | 5023 | 5022 | 0x03,0x06,0x10 | Y | 0 | NA | 148 | 94 |  | N
| DNS Secondary Server address Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45024 | 5024 | 5023 | 0x03,0x06,0x10 | Y | 0 | NA | 149 | 95 |  | N
| Access Level for third IP | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45025 | 5025 | 5024 | 0x03,0x06,0x10 | Y | 0 | NA | 150 | 96 | 0 - None 1 - Read/Write | N
| IP allowlist range3 address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45026 | 5026 | 5025 | 0x03,0x06,0x10 | Y | 0 | NA | 151 | 97 |  | N
| IP allowlist range3 address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45027 | 5027 | 5026 | 0x03,0x06,0x10 | Y | 0 | NA | 152 | 98 |  | N
| IP allowlist range3 address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45028 | 5028 | 5027 | 0x03,0x06,0x10 | Y | 0 | NA | 153 | 99 |  | N
| IP allowlist range3 address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45029 | 5029 | 5028 | 0x03,0x06,0x10 | Y | 0 | NA | 154 | 9A |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45030 | 5030 | 5029 | 0x03,0x06,0x10 | Y | 0 | NA | 155 | 9B |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45031 | 5031 | 5030 | 0x03,0x06,0x10 | Y | 0 | NA | 156 | 9C |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45032 | 5032 | 5031 | 0x03,0x06,0x10 | Y | 0 | NA | 157 | 9D |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45033 | 5033 | 5032 | 0x03,0x06,0x10 | Y | 0 | NA | 158 | 9E |  | N
| Access Level for fourth IP | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45034 | 5034 | 5033 | 0x03,0x06,0x10 | Y | 0 | NA | 159 | 9F | 0 - None 1 - Read/Write | N
| IP allowlist range4 address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45035 | 5035 | 5034 | 0x03,0x06,0x10 | Y | 0 | NA | 160 | A0 |  | N
| IP allowlist range4 address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45036 | 5036 | 5035 | 0x03,0x06,0x10 | Y | 0 | NA | 161 | A1 |  | N
| IP allowlist range4 address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45037 | 5037 | 5036 | 0x03,0x06,0x10 | Y | 0 | NA | 162 | A2 |  | N
| IP allowlist range4 address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45038 | 5038 | 5037 | 0x03,0x06,0x10 | Y | 0 | NA | 163 | A3 |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45039 | 5039 | 5038 | 0x03,0x06,0x10 | Y | 0 | NA | 164 | A4 |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45040 | 5040 | 5039 | 0x03,0x06,0x10 | Y | 0 | NA | 165 | A5 |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45041 | 5041 | 5040 | 0x03,0x06,0x10 | Y | 0 | NA | 166 | A6 |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45042 | 5042 | 5041 | 0x03,0x06,0x10 | Y | 0 | NA | 167 | A7 |  | N
| Access Level for fifth IP | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45043 | 5043 | 5042 | 0x03,0x06,0x10 | Y | 0 | NA | 168 | A8 | 0 - None 1 - Read/Write | N
| IP allowlist range5 address - Byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45044 | 5044 | 5043 | 0x03,0x06,0x10 | Y | 0 | NA | 169 | A9 |  | N
| IP allowlist range5 address - Byte 2 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45045 | 5045 | 5044 | 0x03,0x06,0x10 | Y | 0 | NA | 170 | AA |  | N
| IP allowlist range5 address - Byte 1 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45046 | 5046 | 5045 | 0x03,0x06,0x10 | Y | 0 | NA | 171 | AB |  | N
| IP allowlist range5 address - Byte 0 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45047 | 5047 | 5046 | 0x03,0x06,0x10 | Y | 0 | NA | 172 | AC |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45048 | 5048 | 5047 | 0x03,0x06,0x10 | Y | 0 | NA | 173 | AD |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45049 | 5049 | 5048 | 0x03,0x06,0x10 | Y | 0 | NA | 174 | AE |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45050 | 5050 | 5049 | 0x03,0x06,0x10 | Y | 0 | NA | 175 | AF |  | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45051 | 5051 | 5050 | 0x03,0x06,0x10 | Y | 0 | NA | 176 | B0 |  | N
| RSTP******* | [18 empty] | N
| RSTP Enable/Disable | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45052 | 5052 | 5051 | 0x03,0x06,0x10 | Y | 0 | NA | 177 | B1 | 0 - Disable 1 - Enable | N
| Bridge priority | UINT16 | 2 | 1 | 0 | 15 | 1 | 1 | RW | 45053 | 5053 | 5052 | 0x03,0x06,0x10 | Y | 8 | NA | 178 | B2 |  | N
| Hello Time | UINT16 | 2 | 1 | 1 | 10 | 1 | 1 | RW | 45054 | 5054 | 5053 | 0x03,0x06,0x10 | Y | 2 | Seconds | 179 | B3 |  | N
| Max Age Time | UINT16 | 2 | 1 | 6 | 40 | 1 | 1 | RW | 45055 | 5055 | 5054 | 0x03,0x06,0x10 | Y | 20 | Seconds | 180 | B4 |  | N
| Transmit Hold Count | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45056 | 5056 | 5055 | 0x03,0x06,0x10 | Y | 6 |  | 181 | B5 |  | N
| Forward Delay | UINT16 | 2 | 1 | 4 | 30 | 1 | 1 | RW | 45057 | 5057 | 5056 | 0x03,0x06,0x10 | Y | 15 | Seconds | 182 | B6 |  | N
| RSTP Port 1&2 Settings*********** | [18 empty] | N
| Port 1 Automatic/Manual | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45058 | 5058 | 5057 | 0x03,0x06,0x10 | Y | 1 |  | 183 | B7 | 1 - Automatic 0 - Manual | N
| Port 1 priority | UINT16 | 2 | 1 | 0 | 15 | 1 | 1 | RW | 45059 | 5059 | 5058 | 0x03,0x06,0x10 | Y | 8 | NA | 184 | B8 |  | N
| Port 1 Path Cost | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45060 | 5060 | 5059 | 0x03,0x06,0x10 | Y | 0 | NA | 185 | B9 |  | N
| Port 2 Automatic/Manual | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45061 | 5061 | 5060 | 0x03,0x06,0x10 | Y | 1 |  | 186 | BA | 1 - Automatic 0 - Manual | N
| Port 2 priority | UINT16 | 2 | 1 | 0 | 15 | 1 | 1 | RW | 45062 | 5062 | 5061 | 0x03,0x06,0x10 | Y | 8 | NA | 187 | BB |  | N
| Port 2 Path Cost | UINT16 | 2 | 1 | 0 | 65535 | 1 | 1 | RW | 45063 | 5063 | 5062 | 0x03,0x06,0x10 | Y | 0 | NA | 188 | BC |  | N
| SysLog************ | [18 empty] | N
| SysLog service automatic export | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45064 | 5064 | 5063 | 0x03,0x06,0x10 | Y | 0 |  | 189 | BD | 0-Disable 1-Enable | N
| SysLog Server Address************ | [18 empty] | N
| IP address byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45065 | 5065 | 5064 | 0x03,0x06,0x10 | Y | 0 | NA | 190 | BE |  | N
| IP address byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45066 | 5066 | 5065 | 0x03,0x06,0x10 | Y | 0 | NA | 191 | BF |  | N
| IP address byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45067 | 5067 | 5066 | 0x03,0x06,0x10 | Y | 0 | NA | 192 | C0 |  | N
| IP address byte 3 | UINT16 | 2 | 1 | 0 | 255 | 1 | 1 | RW | 45068 | 5068 | 5067 | 0x03,0x06,0x10 | Y | 0 | NA | 193 | C1 |  | N
| Connection Mode | UINT16 | 2 | 1 | 0 | 2 | 1 | 1 | RW | 45069 | 5069 | 5068 | 0x03,0x06,0x10 | Y | 0 | NA | 194 | C2 | 0- TCP/TLS:6514 1- TCP:801 2- UDP:514 | N
| Syslog Server Port | UINT16 | 2 | 1 | 1 | 65535 | 1 | 1 | RW | 45070 | 5070 | 5069 | 0x03,0x06,0x10 | Y | 6514 | NA | 195 | C3 |  | N
| Export Interval | UINT16 | 2 | 1 | 1 | 3600 | 1 | 1 | RW | 45071 | 5071 | 5070 | 0x03,0x06,0x10 | Y | 60 | seconds | 196 | C4 |  | N
| Modbus Disable / Enable************* | [18 empty] | N
| Modbus HMI Selection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45072 | 5072 | 5071 | 0x03,0x06,0x10 | Y | 1 | NA | 197 | C5 | 0: Disable 1: Enable | N
| Modbus TCP Selection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45073 | 5073 | 5072 | 0x03,0x06,0x10 | Y | 1 | NA | 198 | C6 | 0: Disable 1: Enable | N
| Daylight Saving Settings: For Internal Testing setting is given trhough Modbus *********** | [18 empty] | N
Only applicable for Webservices: Not there in MKT05 | Daylight Saving Selection | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45074 | 5074 | 5073 | 0x03,0x06,0x10 | Y | 0 |  | 199 | C7 | 0:Disable 1:Enable | Y
| Start Day | UINT16 | 2 | 1 | 1 | 5 | 1 | 1 | RW | 45075 | 5075 | 5074 | 0x03,0x06,0x10 | Y | 1 |  | 200 | C8 |  | Y
| Start Week | UINT16 | 2 | 1 | 1 | 7 | 1 | 1 | RW | 45076 | 5076 | 5075 | 0x03,0x06,0x10 | Y | 1 |  | 201 | C9 | 1=Sunday, 2=Monday, 3=Tuesday, 4=Wednsday, 5=Thursday, 6=Friday, 7=Saturday | Y
| Start Month | UINT16 | 2 | 1 | 1 | 12 | 1 | 1 | RW | 45077 | 5077 | 5076 | 0x03,0x06,0x10 | Y | 1 |  | 202 | CA |  | Y
| Start Time | UINT16 | 2 | 1 | 0 | 23 | 1 | 1 | RW | 45078 | 5078 | 5077 | 0x03,0x06,0x10 | Y | 0 |  | 203 | CB |  | Y
| End Day | UINT16 | 2 | 1 | 1 | 5 | 1 | 1 | RW | 45079 | 5079 | 5078 | 0x03,0x06,0x10 | Y | 1 |  | 204 | CC |  | Y
| End Week | UINT16 | 2 | 1 | 1 | 7 | 1 | 1 | RW | 45080 | 5080 | 5079 | 0x03,0x06,0x10 | Y | 1 |  | 205 | CD | 1=Sunday, 2=Monday, 3=Tuesday, 4=Wednsday, 5=Thursday, 6=Friday, 7=Saturday | Y
| End Month | UINT16 | 2 | 1 | 1 | 12 | 1 | 1 | RW | 45081 | 5081 | 5080 | 0x03,0x06,0x10 | Y | 1 |  | 206 | CE |  | Y
| End Time | UINT16 | 2 | 1 | 0 | 23 | 1 | 1 | RW | 45082 | 5082 | 5081 | 0x03,0x06,0x10 | Y | 0 |  | 207 | CF |  | Y
Primary and Secondary NTP/SNTP server name (IP address are in different address)
| primary server name (NTP/SNTP) | UINT16 | 32 | 16 | 0 | 65535 | 1 | 1 | RW | 45083 | 5083 | 5082 | 0x03,0x06,0x10 | Y | 0x7469 0x6D65 0x2E6E 0x6577 0x7365 0x7276 0x6572 0x2E63 0x6F6D |  | 208 | D0 | time.newserver.com | N
| Secondary server name (NTP/SNTP) | UINT16 | 32 | 16 | 0 | 65535 | 1 | 1 | RW | 45099 | 5099 | 5098 | 0x03,0x06,0x10 | Y | 0x7469 0x6D65 0x2E62 0x6163 0x6B75 0x7073 0x6572 0x7665 0x722E 0x636F 0x6D00 |  | 224 | E0 | time.backupserver.com | N
| DNS Enable Disable | UINT16 | 2 | 1 | 0 | 1 | 1 | 1 | RW | 45115 | 5115 | 5114 | 0x03,0x06,0x10 | Y | 1 |  | 240 | F0 | 0:: Obtain IP fron DHCP/BOOTP 1: Manual | N
| reserved | UINT16 | 2 | 1 | 0 | 0 | 1 | 1 | RW | 45116 | 5116 | 5115 | 0x03,0x06,0x10 | Y | 0 |  | 241 | F1 |  | N
Note on T7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: for LTMTEFM and LTMTEBD only Mobus TCP and EIP applicable
Note on T8: Vrund Rana: 1) Modbus TCP-> RSTP only 2) Profinet->MRP only 3) Ethernet/IP-> RSTP or DLR can be choosen Not gauranteed that all can be given on in single firmware
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - Disable 1 - Enable
Note on B33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - V2 1 - V3
Note on B35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - MD5 1 - SHA
Note on B37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - DES 1 - AES
Note on B38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0- Disable 1- Enable
Note on B39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0- Disable 1- Enable
Note on B52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - Disable 1 - Enable
Note on B57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - OFF 1 - -ON
Note on B58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0 - Disable 1 - Enable

## Ethernet Diagnostic Data
| Attribute Name | Size(in Bytes) | Size(in Words) | Min Value | Max Value | Step Size | Multiplier | R/W Access | data Address | Function Codes | Default Value | Units | Remarks
Read Only Data
Ethernet Global Statistics
| Frames Received OK | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43000 | 0x03
| Frames Transmitted OK | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43002 | 0x03
| Reception Error | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43004 | 0x03
| Transmission Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43006 | 0x03
Port 1 Statistics
| Link Speed | 2 | 1 | 0 | 1 | 1 | 1 | R | 43008 | 0x03 | 0 |  | 0: 100 Mbps 1: 10 Mbps 2: Auto Negotiation 3: NA
| Duplex | 2 | 1 | 0 | 1 | 1 | 1 | R | 43009 | 0x03 | 0 |  | 0: Full Duplex 1: Half Duplex 2: Auto Negotiation 3: NA
Port 2 Statistics
| Link Speed | 2 | 1 | 0 | 1 | 1 | 1 | R | 43010 | 0x03 | 0 |  | 0: 100 Mbps 1: 10 Mbps 2: Auto Negotiation 3: NA
| Duplex | 2 | 1 | 0 | 1 | 1 | 1 | R | 43011 | 0x03 | 0 |  | 0: Full Duplex 1: Half Duplex 2: Auto Negotiation 3: NA
pending | Modbus TCP Global Diagnostics
| Port Status | 2 | 1 | 0 | 1 | 1 | 1 | R | 43012 | 0x03 | 0 |  | 0: Not operational; 1: Operational
| Open TCP Connection | 2 | 1 | 0 | 8 | 1 | 1 | R | 43013 | 0x03
| Total Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43014 | 0x03
| Total Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43016 | 0x03
Modbus TCP Port Diagnostics
| Connection 1 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43018 | 0x03
| Connection 1 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43020 | 0x03
| Connection 1 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43021 | 0x03
| Connection 1 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43022 | 0x03
| Connection 1 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43024 | 0x03
| Connection 1 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43026 | 0x03
| Connection 2 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43028 | 0x03
| Connection 2 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43030 | 0x03
| Connection 2 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43031 | 0x03
| Connection 2 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43032 | 0x03
| Connection 2 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43034 | 0x03
| Connection 2 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43036 | 0x03
| Connection 3 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43038 | 0x03
| Connection 3 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43040 | 0x03
| Connection 3 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43041 | 0x03
| Connection 3 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43042 | 0x03
| Connection 3 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43044 | 0x03
| Connection 3 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43046 | 0x03
| Connection 4 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43048 | 0x03
| Connection 4 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43050 | 0x03
| Connection 4 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43051 | 0x03
| Connection 4 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43052 | 0x03
| Connection 4 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43054 | 0x03
| Connection 4 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43056 | 0x03
| Connection 5 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43058 | 0x03
| Connection 5 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43060 | 0x03
| Connection 5 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43061 | 0x03
| Connection 5 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43062 | 0x03
| Connection 5 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43064 | 0x03
| Connection 5 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43066 | 0x03
| Connection 6 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43068 | 0x03
| Connection 6 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43070 | 0x03
| Connection 6 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43071 | 0x03
| Connection 6 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43072 | 0x03
| Connection 6 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43074 | 0x03
| Connection 6 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43076 | 0x03
| Connection 7 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43078 | 0x03
| Connection 7 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43080 | 0x03
| Connection 7 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43081 | 0x03
| Connection 7 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43082 | 0x03
| Connection 7 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43084 | 0x03
| Connection 7 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43086 | 0x03
| Connection 8 Remote IP | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43088 | 0x03
| Connection 8 Remote port | 2 | 1 | 0 | 65536 | 1 | 1 | R | 43090 | 0x03
| Connection 8 Local Port | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43091 | 0x03
| Connection 8 Received Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43092 | 0x03
| Connection 8 Transmitted Messages | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43094 | 0x03
| Connection 8 Sent Errors | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43096 | 0x03
Modbus RTU Statistics
| Frames Received | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43098 | 0x03
| Frames Transmitted | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43100 | 0x03
| Baudrate | 2 | 1 | 0 | 6 | 1 | 1 | R | 43102 | 0x03 |  |  | 0 = 2400 1 = 4800 2 = 9600 3= 19200 4 = 38400 5 = 57600 6 = 115200
| Parity | 2 | 1 | 0 | 2 | 1 | 1 | R | 43103 | 0x03 |  |  | 0 = None 1 = ODD 2 = EVEN
| Stop Bit | 2 | 1 | 0 | 2 | 1 | 1 | R | 43104 | 0x03 |  |  | 0 = 0 1 = 1 2 = 2
| Slave ID | 2 | 1 | 1 | 247 | 1 | 1 | R | 43105 | 0x03
pending | Redundancy Stats
| Bridge Status | 2 | 1 | 0 | 1 | 1 | 1 | R | 43106 | 0x03 |  |  | 0-1 stesp size 1 (enable/disable)
| Bridge ID | 16 | 8 | 1 | 65535 | 1 | 1 | R | 43107 | 0x03
| Root ID | 16 | 8 | 1 | 65535 | 1 | 1 | R | 43115 | 0x03
| Root Port | 2 | 1 | 1 | 65535 | 1 | 1 | R | 43123 | 0x03
| Root Path Cost | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43124 | 0x03
| Total Topology change | 2 | 1 | 1 | 65535 | 1 | 1 | R | 43125 | 0x03
| Configured Bridge Hello Time | 2 | 1 | 1 | 10 | 1 | 1 | R | 43126 | 0x03
| Learned Bridge Hello Time | 2 | 1 | 1 | 10 | 1 | 1 | R | 43127 | 0x03
| Configured Bridge Forward Delay | 2 | 1 | 4 | 30 | 1 | 1 | R | 43128 | 0x03
| Learned Bridge Forward Delay | 2 | 1 | 4 | 30 | 1 | 1 | R | 43129 | 0x03
| Configured Bridge Max Age Time | 2 | 1 | 6 | 40 | 1 | 1 | R | 43130 | 0x03
| Learned Bridge Max Age Time | 2 | 1 | 6 | 40 | 1 | 1 | R | 43131 | 0x03
| Port 1 State | 2 | 1 | 0 | 5 | 1 | 1 | R | 43132 | 0x03
| Port 1 Role | 2 | 1 | 0 | 3 | 1 | 1 | R | 43133 | 0x03
| Port 1 Priority | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43134 | 0x03 |  |  | 0-15 step size 1
| Port 1 Path Cost | 2 | 1 | 0 | 4294967295 | 1 | 1 | R | 43135 | 0x03 |  |  | 0- 200000000 stepsize 1
| Received RST | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43136 | 0x03
| Transmitted RST | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43138 | 0x03
| Received TCN | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43140 | 0x03
| Transmitted TCN | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43142 | 0x03
| Port 2 State | 2 | 1 | 0 | 5 | 1 | 1 | R | 43144 | 0x03
| Port 2 Role | 2 | 1 | 0 | 3 | 1 | 1 | R | 43145 | 0x03
| Port 2 Priority | 2 | 1 | 0 | 65535 | 1 | 1 | R | 43146 | 0x03 |  |  | 0-15 step size 1 (15*4096)
| Port 2 Path Cost | 2 | 1 | 0 | 4294967295 | 1 | 1 | R | 43147 | 0x03 |  |  | 0- 200000000 stepsize 1
| Received RST | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43148 | 0x03
| Transmitted RST | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43150 | 0x03
| Received TCN | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43152 | 0x03
| Transmitted TCN | 4 | 2 | 0 | 4294967295 | 1 | 1 | R | 43154 | 0x03
Date & Time Stats
| Time Source | 2 | 1 | 0 | 3 | 1 | 1 | R | 43156 | 0x03 |  |  | 0: Manual; 1: NTP; 2: FB
| Last Synchronised | 12 | 6 | 0 | 1 | 1 | 1 | R | 43157 | 0x03
| NTP Synchronization status | 2 | 1 | 0 | 1 | 1 | 1 | R | 43163 | 0x03 |  |  | 0: Not synchronised; 1: Synchronised