## RDOL
S.No. | Title | Description | Pre-Conditions | Step Action | Step Expected Result | Step Notes | Expected Result
1 | To Verify the input and output assembly of tera profile | Verify EtherNet/IP connection establishment using required communication parameters. Validate successful communication between client and device. Verify Input Assembly data mapping and reception. Verify Output Assembly data mapping and transmission. Test Input and Output assemblies with different data combinations and configurations. Ensure correct cyclic data exchange as per the selected EIP profile. | 1.Connect main module to Sensor module with RJ11 cable & display with main module using RJ45 cable. 2. Make sure that all available expansion modules connected to main module & power ON the device. 3. Connect main module Ethernet port with PC Ethernet port with Ethernet Cat-7 cable. 4. In HMI, configure starter-RDOL, Protocol selection -Ethernet IP and IP configuration - DHCP, IP address - 169.254.217.162 (Fallback IP) with subnet mask 255.255.0.0, Client IP address is 169.254.217.145 and Profile selection- Tera Profile. | Add device in the EIP scan and add Class1 Connection with input data size 40 and output data size 4, input instance 117 and output instance 107. | Ethernet Connection establish properly for the Tera Profile and data update properly. |  | Step 1 For Tera Profile Etherenet Connection establish properly Pass/Fail Criteria-Expected result✅ Pass: Ethernet Connection establish properly for the Tera Profile. ❌ Fail: Connection does not establishes. Step 2 For Tera profile motor run in forward direction. Motor and metering status is update properly. Motor gets stop after transfer stop command. Event log update properly. Pass/Fail Criteria-Expected result✅ Pass: Motor run in forward and respective data update in input assembly.Motor gets stop. Events update. ❌ Fail: After send command motor does not run. respective Motor status and metering is not update. Motor does not get stop. Event data is not update properly. Step 3 For Tera profile motor run in reverse direction. After transfer the mode selection command motor gets stop and stop cause update properly. And events update. Pass/Fail Criteria-Expected result✅ Pass: Motor run in reverse. Motor stop after send mode selection command and events update. ❌ Fail: Motor does not run in reverse direction. motor does not stop after mode transer and stop cause and evets does not update properly. Step 4 For Tera profile motor run in reverse direction. mode transfers properly after send command. Alarm and trip status update properly. And events update. Pass/Fail Criteria-Expected result✅ Pass: Motor run in reverse. motor does not stop after mode transfer. Alarm and trip status update and events update. ❌ Fail: Motor does not run in reverse direction. motor gets stop after mode transer and alarm and trip status and evets does not update properly. Step 5 For Self test with trip command self test complete with respective led pattern and DO operate. For self trip without trip only led pattern reflected. And after send logic test command logic test completed with device led is blinking in green. Pass/Fail Criteria-Expected result✅ Pass: Self test complete properly, for self tests led pattern reflect properly and for without trip condition DO operate. and logic test complete with device led is blinking in green. ❌ Fail:Test does not perform, led status does not update, Events data does not update. Step 6 After send the commands functionality of each command works properly. Event log for each command. Pass/Fail Criteria-Expected result✅ Pass: According to functionality parameters gets reset and events log for function. ❌ Fail: Functionality of command does not work. event does not log. Step 7 After send the commands functionality of each command works properly. Event log for each command. Pass/Fail Criteria-Expected result✅ Pass: Functinality works properly and events log for function. ❌ Fail: Functionality of command does not work. event does not log.
1 | To Verify the input and output assembly of tera profile |  |  | Start the motor with Forward start command using Output assembly of tera profile. Verify with Momentary and Maintained mode of Comm Start I/P. Send the motor stop command with output assembly. | Motor run in forward direction. Verified motor status and metering data. Motor gets stop when send the stop command (in momentary mode).
1 | To Verify the input and output assembly of tera profile |  |  | Start the motor with Reverse start command. Configure mode transfer as bump and transfer Mode selection 1 and Mode selection 2 commands using output assembly. | Motor run in reverse direction. After give Mode selection command motor stop and stop cause update.
1 | To Verify the input and output assembly of tera profile |  |  | Start the motor with Reverse start command. Configure mode transfer as bumpless and transfer Mode selection 1 and Mode selection 2 commands using output assembly. Configure the protection settings to the alarm and trip functions. Inject the fault condition while motor is in running state. | Motor run in reverse direction. Mode tranfers properly after send command. After fault condition is injected alarm and trip status update according to the configuration.
1 | To Verify the input and output assembly of tera profile |  |  | Send self test and logic test commands with output assembly | For Self test with trip command self test complete with respective led pattern and DO operate. For self trip without trip only led pattern reflected. And after send logic test command logic test completed with device led is blinking in green.
1 | To Verify the input and output assembly of tera profile |  |  | Send reset commands one by one with output assembly. ( Clear all command Reset Inhibit command Reset no of starts command Reset no of stops command Clear Energy command Reset run hour command Clear thermal capacity level command Clear Trip counter command) | After send the commands functionality of each command works properly. Event log for each command.
1 | To Verify the input and output assembly of tera profile |  |  | Send permissive commands with output assembly | After send the commands functionality of each command works properly. Event log for each command.
2 | To Verify the input and output assembly of Tera Basic Overload profile | Verify EtherNet/IP connection establishment using required communication parameters. Validate successful communication between client and device. Verify Input Assembly data mapping and reception. Verify Output Assembly data mapping and transmission. Test Input and Output assemblies with different data combinations and configurations. Ensure correct cyclic data exchange as per the selected EIP profile. | 1.Connect main module to Sensor module with RJ11 cable & display with main module using RJ45 cable. 2. Make sure that all available expansion modules connected to main module & power ON the device. 3. Connect main module Ethernet port with PC Ethernet port with Ethernet Cat-7 cable. 4. In HMI, configure starter-RDOL, Protocol selection -Ethernet IP and IP configuration - DHCP, IP address - 169.254.217.162 (Fallback IP) with subnet mask 255.255.0.0, Client IP address is 169.254.217.145 and Profile selection- Tera Basic Overload Profile. | Add device in the EIP scan and add Class1 Connection with input data size 1 and output data size 1, input instance 50 and output instance 2. | Ethernet Connection establish properly for the Tera Basic Overload Profile and data update properly. |  | Step 1 For Tera Basic Overload Profile Etherenet Connection establish properly Pass/Fail Criteria-Expected result✅ Pass: Ethernet Connection establish properly for the Tera Basic Overload Profile. ❌ Fail: Connection does not establishes. Step 2 After device gets trip, trip bit update in the input assembly and DO and led update trip status and event data log. Pass/Fail Criteria-Expected result✅ Pass: After device gets trip, trip bit update in the input assembly and event data update. ❌ Fail: Input assembly does not update the trip status. DO does not opearate. led does not reflect trip status. event data does not log. Step 3 After send the command trip gets reset, DO and led reset and event log for trip reset. Pass/Fail Criteria-Expected result✅ Pass: DO and led gets reset and event for the trip reset gets log. ❌ Fail: DO and led does not get reset, Event does not update.
2 | To Verify the input and output assembly of Tera Basic Overload profile |  |  | Configure protection setting to trip function and Trip reset mode as Comm, start the motor via HMI and Inject fault condition while motor is in running state. | After delay time completed device gets trip, DO operates and led reflects trip status. Trip bit update in the input assembly.
2 | To Verify the input and output assembly of Tera Basic Overload profile |  |  | Send trip reset command with output assembly. | After send the command trip gets reset, DO and led reset and event log for trip reset.
3 | To Verify the input and output assembly of Tera Extended Overload profile | Verify EtherNet/IP connection establishment using required communication parameters. Validate successful communication between client and device. Verify Input Assembly data mapping and reception. Verify Output Assembly data mapping and transmission. Test Input and Output assemblies with different data combinations and configurations. Ensure correct cyclic data exchange as per the selected EIP profile. | 1.Connect main module to Sensor module with RJ11 cable & display with main module using RJ45 cable. 2. Make sure that all available expansion modules connected to main module & power ON the device. 3. Connect main module Ethernet port with PC Ethernet port with Ethernet Cat-7 cable. 4. In HMI, configure starter-RDOL, Protocol selection -Ethernet IP and IP configuration - DHCP, IP address - 169.254.217.162 (Fallback IP) with subnet mask 255.255.0.0, Client IP address is 169.254.217.145 and Profile selection- Tera Extended Overload. | Add device in the EIP scan and add Class1 Connection with input data size 1 and output data size 1, input instance 51 and output instance 2. | Ethernet Connection establish properly for the Tera Extended Overload and data update properly. |  | Step 1 For Tera Extended Overload Profile Etherenet Connection establish properly Pass/Fail Criteria-Expected result✅ Pass: Ethernet Connection establish properly for the Tera Extended Overload Profile. ❌ Fail: Connection does not establishes. Step 2 Alarm bit update and after device gets trip, trip bit update in the input assembly and DO and led update trip status and event data log. Pass/Fail Criteria-Expected result✅ Pass: After device gets alarm and trip, trip bit update in the input assembly and event data update. ❌ Fail: Input assembly does not update the alarm and trip status. DO does not opearate. led does not reflect trip status. event data does not log. Step 3 After send the command trip gets reset, DO and led reset and event log for trip reset. Pass/Fail Criteria-Expected result✅ Pass: DO and led gets reset and event for the trip reset gets log. ❌ Fail: DO and led does not get reset, Event does not update.
3 | To Verify the input and output assembly of Tera Extended Overload profile |  |  | Configure protection setting to trip and alarm function and Trip reset mode as Comm, start the motor via HMI and Inject fault condition while motor is in running state. | After inject fault condition Alarm status update and after complete delay time device gets trip, DO operates and led reflects trip status. Trip bit update in the input assembly.
3 | To Verify the input and output assembly of Tera Extended Overload profile |  |  | Send trip reset command with output assembly. | After send the command trip gets reset, DO and led reset and event log for trip reset.
4 | To Verify the input and output assembly of Tera Basic Motor Starter profile | Verify EtherNet/IP connection establishment using required communication parameters. Validate successful communication between client and device. Verify Input Assembly data mapping and reception. Verify Output Assembly data mapping and transmission. Test Input and Output assemblies with different data combinations and configurations. Ensure correct cyclic data exchange as per the selected EIP profile. | 1.Connect main module to Sensor module with RJ11 cable & display with main module using RJ45 cable. 2. Make sure that all available expansion modules connected to main module & power ON the device. 3. Connect main module Ethernet port with PC Ethernet port with Ethernet Cat-7 cable. 4. In HMI, configure starter-RDOL, Protocol selection -Ethernet IP and IP configuration - DHCP, IP address - 169.254.217.162 (Fallback IP) with subnet mask 255.255.0.0, Client IP address is 169.254.217.145 and Profile selection- Tera Basic Motor Starter. | Add device in the EIP scan and add Class1 Connection with input data size 1 and output data size 1, input instance 52 and output instance 3. | Ethernet Connection establish properly for the Tera Basic Motor Starter and data update properly. |  | Step 1 For Tera Basic Motor Starter Profile Etherenet Connection establish properly Pass/Fail Criteria-Expected result✅ Pass: Ethernet Connection establish properly for the Tera Basic Motor Starter Profile. ❌ Fail: Connection does not establishes.
4 | To Verify the input and output assembly of Tera Basic Motor Starter profile |  |  | Start the motor with Forward start command using Output assembly of tera profile. Verify with Momentary and Maintained mode of Comm Start I/P. Chcek the motor running 1 bit of input assembly. | Motor run in forward direction. Motor status update in the input assembly for both modes of Comm start I/P.
4 | To Verify the input and output assembly of Tera Basic Motor Starter profile
5 | To Verify the input and output assembly of Tera Extended Contactor | Verify EtherNet/IP connection establishment using required communication parameters. Validate successful communication between client and device. Verify Input Assembly data mapping and reception. Verify Output Assembly data mapping and transmission. Test Input and Output assemblies with different data combinations and configurations. Ensure correct cyclic data exchange as per the selected EIP profile. | 1.Connect main module to Sensor module with RJ11 cable & display with main module using RJ45 cable. 2. Make sure that all available expansion modules connected to main module & power ON the device. 3. Connect main module Ethernet port with PC Ethernet port with Ethernet Cat-7 cable. 4. In HMI, configure starter-RDOL, Protocol selection -Ethernet IP and IP configuration - DHCP, IP address - 169.254.217.162 (Fallback IP) with subnet mask 255.255.0.0, Client IP address is 169.254.217.145 and Profile selection- Tera Basic Motor Starter.
5 | To Verify the input and output assembly of Tera Extended Contactor